Chapter 17 Special Inspections and Tests

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE
CHAPTER 17 — SPECIAL INSPECTIONS AND TESTS

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC- CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  | X |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) | X |  |  | X | X |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1701 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1701.1.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1701.1.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1701.1.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1702 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1703 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1703.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1704.2 |  |  |  | X | X |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1704.2.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1704.2.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1704.2.5.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1704.3.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.2.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.4.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.5.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.7 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.2.8 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3 |  |  | X |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| Table 1705.3 |  |  | X |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.3.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.5 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.6 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.7 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.8 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.9 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.9.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.3.9.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.4.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.4.1.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.5.3 |  |  | X |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| Table 1705.5.3 |  |  | X |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.5.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.5.5 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.5.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.5.7 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.6.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.7.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.12.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.12.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.13.1.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.13.1.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.13.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.13.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.14.1.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.14.1.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.14.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.14.3.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.15 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.16 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1705.18 |  |  | X |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1705.19 — 1705.20 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1707.1 | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1710 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 17 provides a variety of procedures and criteria for testing materials and assemblies, and labeling materials and assemblies. Its key purposes are to establish where additional inspections/observations and testing must be provided, and the submittals and verifications that must be provided to the building official. This chapter expands on the inspections of Chapter 1 by requiring special inspection by a qualified individual where indicated and, in some cases, structural observation by a registered design professional. Quality assurance measures that verify proper assembly of structural components and the suitability of the installed materials are intended to provide a building that, once constructed, complies with the minimum structural and fire-resistance code requirements as well as the approved design. To determine this compliance often requires frequent inspections and testing at specific stages of construction.

ICC code development note: Code change proposals to sections preceded by the designation [BF] will be considered by the IBC—Fire Safety Code Development Committee during the 2024 (Group A) Code Development Cycle. Sections preceded by the designation [F] will be considered by the International Fire Code Development Committee during the 2024 (Group A) Code Development Cycle. All other code change proposals will be considered by the IBC—Structural Code Development Committee during the Group B cycle.

Section 1701 General

1701.1 Scope

The provisions of this chapter shall govern the quality, workmanship and requirements for materials covered. Materials of construction and tests shall conform to the applicable standards listed in this code.

1701.1.1 Application

[OSHPD] The scope of application of Chapter 17 is as follows:

Structures regulated by the Department of Health Care Access and Information/Office of Statewide Hospital Planning and Development (OSHPD), which include hospital buildings removed from general acute care service, skilled nursing facility buildings, intermediate care facility buildings and acute psychiatric hospital buildings as listed in Sections 1.10.1, 1.10.2 and 1.10.5.

1701.1.2 Amendments in This Chapter

[OSHPD] OSHPD adopts this chapter as amended.

1701.1.3 Identification of Amendments

[OSHPD 1R, 2 & 5] Office of Statewide Hospital Planning and Development (OSHPD) amendments appear in this chapter preceded with the appropriate acronym, as follows:

- [OSHPD 1R] — For applications listed in Section 1.10.1.

- [OSHPD 2] — For applications listed in Section 1.10.2.

- [OSHPD 5] — For applications listed in Section 1.10.5.

Section 1702 New Materials

1702.1 General

New building materials, equipment, appliances, systems or methods of construction not provided for in this code, and any material of questioned suitability proposed for use in the construction of a building or structure, shall be subjected to the tests prescribed in this chapter and in the approved rules to determine character, quality and limitations of use.

Section 1703 Approvals

1703.1 Approved Agency

An approved agency shall provide all information as necessary for the building official to determine that the agency meets the applicable requirements specified in Sections 1703.1.1 through 1703.1.3.

1703.1.1 Independence

An approved agency shall be objective, competent and independent from the contractor responsible for the work being inspected. The agency shall disclose to the building official and the registered design professional in responsible charge possible conflicts of interest so that objectivity can be confirmed.

1703.1.2 Equipment

An approved agency shall have adequate equipment to perform required tests. The equipment shall be periodically calibrated.

1703.1.3 Personnel

An approved agency shall employ experienced personnel educated in conducting, supervising and evaluating tests and special inspections.

1703.2 Written Approval

Any material, appliance, equipment, system or method of construction meeting the requirements of this code shall be approved in writing after satisfactory completion of the required tests and submission of required test reports.

1703.3 Record of Approval

For any material, appliance, equipment, system or method of construction that has been approved, a record of such approval, including the conditions and limitations of the approval, shall be kept on file in the building official's office and shall be available for public review at appropriate times.

1703.4 Performance

Specific information consisting of test reports conducted by an approved agency in accordance with the appropriate referenced standards, or other such information as necessary, shall be provided for the building official to determine that the product, material or assembly meets the applicable code requirements.

[OSHPD 1R, 2 & 5] Tests performed by an independent approved testing agency/laboratory or under the responsible charge of a competent approved independent Registered Design Professional shall be deemed to comply with requirements of this section. Test reports for structural tests shall be reviewed and accepted by an independent California licensed structural engineer.

1703.4.1 Research and Investigation

Sufficient technical data shall be submitted to the building official to substantiate the proposed use of any product, material or assembly. If it is determined that the evidence submitted is satisfactory proof of performance for the use intended, the building official shall approve the use of the product, material or assembly subject to the requirements of this code. The costs, reports and investigations required under these provisions shall be paid by the owner or the owner's authorized agent.

1703.4.2 Research Reports

Supporting data, where necessary to assist in the approval of products, materials or assemblies not specifically provided for in this code, shall consist of valid research reports from approved sources.

1703.5 Labeling

Products, materials or assemblies required to be labeled shall be labeled in accordance with the procedures set forth in Sections 1703.5.1 through 1703.5.4.

1703.5.1 Testing

An approved agency shall test a representative sample of the product, material or assembly being labeled to the relevant standard or standards. The approved agency shall maintain a record of the tests performed. The record shall provide sufficient detail to verify compliance with the test standard.

1703.5.2 Inspection and Identification

The approved agency shall periodically perform an inspection, which shall be in-plant if necessary, of the product or material that is to be labeled. The inspection shall verify that the labeled product, material or assembly is representative of the product, material or assembly tested.

1703.5.3 Label Information

The label shall contain the manufacturer's identification, model number, serial number or definitive information describing the performance characteristics of the product, material or assembly and the approved agency's identification.

1703.5.4 Method of Labeling

Information required to be permanently identified on the product, material or assembly shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed.

1703.6 Evaluation and Follow-Up Inspection Services

Where structural components or other items regulated by this code are not visible for inspection after completion of a prefabricated assembly, the owner or the owner's authorized agent shall submit a report of each prefabricated assembly. The report shall indicate the complete details of the assembly, including a description of the assembly and its components, the basis upon which the assembly is being evaluated, test results and similar information and other data as necessary for the building official to determine conformance to this code. Such a report shall be approved by the building official.

1703.6.1 Follow-Up Inspection

The owner or the owner's authorized agent shall provide for special inspections of fabricated items in accordance with Section 1704.2.5.

1703.6.2 Test and Inspection Records

Copies of necessary test and special inspection records shall be filed with the building official.

Section 1704 Special Inspections and Tests, Contractor Responsibility and Structural Observation

1704.1 General

Special inspections and tests, statements of special inspections, responsibilities of contractors, submittals to the building official and structural observations shall meet the applicable requirements of this section.

1704.2 Special Inspections and Tests

Where application is made to the building official for construction as specified in Section 105, or 1.8.4, as applicable, the owner or the owner's authorized agent, other than the contractor, shall employ one or more approved agencies to provide special inspections and tests during construction on the types of work specified in Section 1705 and identify the approved agencies to the building official. These special inspections and tests are in addition to the inspections by the building official that are identified in Section 110.

[OSHPD 1R, 2 & 5] In addition, the approved agencies shall provide special inspections and tests during construction on the types of work listed under Chapters 14, 15, 17, 18, 19, 20, 21, 22, 23, 24 and 25, and noted in the Test, Inspection and Observation (TIO) program as required by the Office.

The special inspectors shall act under the direction of the architect or structural engineer or both, and be responsible to the Owner. Where California Administrative Code Section 7-115 (a) 2 permits construction documents to be prepared under the responsible charge of a mechanical, electrical or civil engineer, special inspectors shall be permitted to work under the direction of an engineer in the appropriate branch as permitted therein.

Exceptions:

- Special inspections and tests are not required for construction of a minor nature or as warranted by conditions in the jurisdiction as approved by the building official.

- Unless otherwise required by the building official, special inspections and tests are not required for Group U occupancies that are accessory to a residential occupancy including, but not limited to, those listed in Section 312.1.

- Special inspections and tests are not required for portions of structures designed and constructed in accordance with the cold-formed steel light-frame construction provisions of Section 2206.1.2 or the conventional light-frame construction provisions of Section 2308. [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- The contractor is permitted to employ the approved agencies where the contractor is also the owner. [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- [HCD 1] The provisions of Health and Safety Code Division 13, Part 6 and the California Code of Regulations, Title 25, Division 1, Chapter 3, commencing with Section 3000, shall apply to the construction and inspection of factory-built housing as defined in Health and Safety Code Section 19971.

1704.2.1 Special Inspector Qualifications

Prior to the start of the construction, the approved agencies shall provide written documentation to the building official demonstrating the competence and relevant experience or training of the special inspectors who will perform the special inspections and tests during construction. Experience or training shall be considered to be relevant where the documented experience or training is related in complexity to the same type of special inspection or testing activities for projects of similar complexity and material qualities. These qualifications are in addition to qualifications specified in other sections of this code.

The registered design professional in responsible charge and engineers of record involved in the design of the project are permitted to act as an approved agency and their personnel are permitted to act as special inspectors for the work designed by them, provided they qualify as special inspectors.

1704.2.2 Access for Special Inspection

The construction or work for which special inspection or testing is required shall remain accessible and exposed for special inspection or testing purposes until completion of the required special inspections or tests.

1704.2.3 Statement of Special Inspections

The applicant shall submit a statement of special inspections in accordance with Section 107.1 as a condition for permit issuance. This statement shall be in accordance with Section 1704.3.

Exception: A statement of special inspections is not required for portions of structures designed and constructed in accordance with the cold-formed steel light-frame construction provisions of Section 2206.1.2 or the conventional light-frame construction provisions of Section 2308. [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

1704.2.4 Report Requirement

Approved agencies shall keep records of special inspections and tests. The approved agency shall submit reports of special inspections and tests to the building official and to the registered design professional in responsible charge at frequencies required by the approved construction documents or building official. All reports shall describe the nature and extent of inspections and tests, the location where the inspections and tests were performed, and indicate that work inspected or tested was or was not completed in conformance to approved construction documents. Discrepancies shall be brought to the immediate attention of the contractor for correction. If they are not corrected, the discrepancies shall be brought to the attention of the building official and to the registered design professional in responsible charge prior to the completion of that phase of the work. A final report documenting required special inspections and tests, and correction of any discrepancies noted in the inspections or tests, shall be submitted at a point in time agreed upon prior to the start of work by the owner or the owner's authorized agent to the building official. [OSHPD 1R, 2 & 5] Report requirement shall be per 1704A.2.4.

1704.2.5 Special Inspection of Fabricated Items

Where fabrication of structural, load-bearing or lateral load-resisting members or assemblies is being conducted on the premises of a fabricator's shop, special inspections of the fabricated items shall be performed during fabrication, except where the fabricator has been approved to perform work without special inspections in accordance with Section 1704.2.5.1.

1704.2.5.1 Fabricator Approval

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Special inspections during fabrication are not required where the work is done on the premises of a fabricator approved to perform such work without special inspection. Approval shall be based on review of the fabricator's written fabrication procedures and quality control manuals that provide a basis for control of materials and workmanship, with periodic auditing of fabrication and quality control practices by an approved agency or the building official. At completion of fabrication, the approved fabricator shall submit a certificate of compliance to the owner or the owner's authorized agent for submittal to the building official as specified in Section 1704.5 stating that the work was performed in accordance with the approved construction documents.

1704.3 Statement of Special Inspections

Where special inspections or tests are required by Section 1705, the registered design professional in responsible charge shall prepare a statement of special inspections in accordance with Section 1704.3.1 for submittal by the applicant in accordance with Section 1704.2.3.

Exception: The statement of special inspections is permitted to be prepared by a qualified person approved by the building official for construction not designed by a registered design professional.

1704.3.1 Content of Statement of Special Inspections

The statement of special inspections shall identify the following:

- The materials, systems, components and work required to have special inspections or tests by the building official or by the registered design professional responsible for each portion of the work.

- The type and extent of each special inspection.

- The type and extent of each test.

- Additional requirements for special inspections or tests for seismic or wind resistance as specified in Sections 1705.12, 1705.13 and 1705.14.

- For each type of special inspection, identification as to whether it will be continuous special inspection, periodic special inspection or performed in accordance with the notation used in the referenced standard where the inspections are defined.

- Deferred submittal items that require a supplemental statement of special inspections.

1704.3.2 Seismic Requirements in the Statement of Special Inspections

Where Section 1705.13 or 1705.14 specifies special inspections or tests for seismic resistance, the statement of special inspections shall identify the designated seismic systems and seismic force-resisting systems that are subject to the special inspections or tests. [OSHPD 1R, 2 & 5] Where Section 1705.13 or 1705.14 specifies special inspections or tests for seismic resistance, the statement of special inspections shall identify the equipment/components that require special seismic certification and seismic force-resisting systems that are subject to the special inspection or tests.

1704.3.3 Wind Requirements in the Statement of Special Inspections

Where Section 1705.12 specifies special inspection for wind resistance, the statement of special inspections shall identify the main windforce-resisting systems and wind-resisting components that are subject to special inspections.

1704.4 Contractor Responsibility

Each contractor responsible for the construction of a main wind- or seismic force-resisting system, designated seismic system or a wind- or seismic force-resisting component listed in the statement of special inspections shall submit a written statement of responsibility to the building official and the owner or the owner's authorized agent prior to the commencement of work on the system or component. The contractor's statement of responsibility shall contain acknowledgement of awareness of the special requirements contained in the statement of special inspections.

1704.5 Submittals to the Building Official

In addition to the submittal of reports of special inspections and tests in accordance with Section 1704.2.4, reports and certificates shall be submitted by the owner or the owner's authorized agent to the building official for each of the following:

- Certificates of compliance for the fabrication of structural, load-bearing or lateral load-resisting members or assemblies on the premises of an approved fabricator in accordance with Section 1704.2.5.1.

- Certificates of compliance for the seismic qualification of nonstructural components, supports and attachments in accordance with Section 1705.14.2.

- Certificates of compliance for designated seismic systems in accordance with Section 1705.14.3.

- Reports of preconstruction tests for shotcrete in accordance with ACI 318.

- Certificates of compliance for open web steel joists and joist girders in accordance with Section 2207.5.

- Reports of material properties verifying compliance with the requirements of AWS D1.4 for weldability as specified in Section 26.6.4 of ACI 318 for reinforcing bars in concrete complying with a standard other than ASTM A706 that are to be welded.

- Reports of mill tests in accordance with Section 20.2.2.5 of ACI 318 for reinforcing bars complying with ASTM A615 and used to resist earthquake-induced flexural or axial forces in the special moment frames, special structural walls or coupling beams connecting special structural walls of seismic force-resisting systems in structures assigned to Seismic Design Category B, C, D, E or F.

1704.6 Structural Observations

Where required by the provisions of Section 1704.6.1, the owner or the owner's authorized agent shall employ a registered design professional to perform structural observations. The structural observer shall visually observe representative locations of structural systems, details and load paths for general conformance to the approved construction documents. Structural observation does not include or waive the responsibility for the inspections in Section 110 or the special inspections in Section 1705 or other sections of this code. Prior to the commencement of observations, the structural observer shall submit to the building official a written statement identifying the frequency and extent of structural observations. At the conclusion of the work included in the permit, the structural observer shall submit to the building official a written statement that the site visits have been made and identify any reported deficiencies that, to the best of the structural observer's knowledge, have not been resolved.

1704.6.1 Structural Observations for Structures

Structural observations shall be provided for those structures where one or more of the following conditions exist:

- The structure is classified as Risk Category III or IV.

- The structure is a high-rise building.

- The structure is assigned to Seismic Design Category E, and is greater than two stories above grade plane.

- Such observation is required by the registered design professional responsible for the structural design.

- Such observation is specifically required by the building official.

Section 1705 Required Special Inspections and Tests

1705.1 General

Special inspections and tests of elements and nonstructural components of buildings and structures shall meet the applicable requirements of this section.

1705.1.1 Special Cases

Special inspections and tests shall be required for proposed work that is, in the opinion of the building official, unusual in its nature, such as, but not limited to, the following examples:

- Construction materials and systems that are alternatives to materials and systems prescribed by this code.

- Unusual design applications of materials described in this code.

- Materials and systems required to be installed in accordance with additional manufacturer's instructions that prescribe requirements not contained in this code or in standards referenced by this code.

1705.2 Steel Construction

The special inspections and nondestructive testing of steel construction in buildings, structures and portions thereof shall be in accordance with this section.

Exception: Special inspections of the steel fabrication process shall not be required where the fabrication process for the entire building or structure does not include any welding, thermal cutting or heating operation of any kind. In such cases, the fabricator shall be required to submit a detailed procedure for material control that demonstrates the fabricator's ability to maintain suitable records and procedures such that, at any time during the fabrication process, the material specification and grade for the main stress-carrying elements are capable of being determined. Mill test reports shall be identifiable to the main stress-carrying elements where required by the approved construction documents.

1705.2.1 Structural Steel

Special inspections and nondestructive testing of structural steel elements in buildings, structures and portions thereof shall be in accordance with the quality assurance inspection requirements of AISC 360. [OSHPD 1R, 2 & 5] and this code.

Exception: Special inspection of railing systems composed of structural steel elements shall be limited to welding inspection of welds at the base of cantilevered rail posts.

[OSHPD 1R, 2 & 5] The following provisions of AISC 360, Chapter N are not permitted:

- N5, Item 3 (Coordinated Inspection).

- N6 (Approved Fabricators and Erectors).

Notes: [OSHPD 1R, 2 & 5]

- Quality assurance requirements in AISC 360, AISC 341, AISC 358, AISO S240, SDI QA/QC and AISC 370 are equivalent to special inspection and testing requirements in this code and are provided by approved agencies employed by the Owner.

- Chapter 22 requires the steel fabrication and erection, including quality control, to be in accordance with the AISC 360, AISC 341, AISC 358, AISI S240, SDI QA/QC and AISC 370.

1705.2.2 Structural Stainless Steel

Special inspections and nondestructive testing of structural stainless steel elements in buildings and portions thereof shall be in accordance with the quality assurance inspection requirements of AISC 370. [OSHPD 1R, 2 & 5] and this code.

[OSHPD 1R, 2 & 5] The following provisions of AISC 370, Chapter N are not permitted:

- N5, Item 3. (Coordinated Inspection).

- N6 (Approved Fabricators and Erectors).

1705.2.3 Cold-Formed Steel Deck

Special inspections and qualification of welding special inspectors for cold-formed steel floor and roof deck shall be in accordance with the quality assurance inspection requirements of SDI QA/QC. [OSHPD 1R, 2 & 5] and this code.

[OSHPD 1R, 2 & 5] SDI QA/QC Section D3 (Coordinated Inspection) is not permitted.

1705.2.4 Open-Web Steel Joists and Joist Girders

Special inspections of open-web steel joists and joist girders in buildings, structures and portions thereof shall be in accordance with Table 1705.2.4.

TABLE 1705.2.4—REQUIRED SPECIAL INSPECTIONS OF OPEN-WEB STEEL JOISTS AND JOIST GIRDERS

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARDa |
| --- | --- | --- | --- |
| 1. Installation of open-web steel joists and joist girders. |  |  |  |
| a. End connections — welding or bolted. | — | X | SJI specifications listed in Section 2207.1. |
| b. Bridging — horizontal or diagonal. | — | — | — |
| 1. Standard bridging. | — | X | SJI specifications listed in Section 2207.1. |
| 2. Bridging that differs from the SJI specifications listed in Section 2207.1. | — | X | — |

- Where applicable, see Section 1705.13.

1705.2.4.1 Steel Joist and Joist Girder Inspection

[OSHPD 1R, 2 & 5] Special inspection is required during the manufacture and welding of steel joists or joist girders. The approved agency shall verify that proper quality control procedures and tests have been employed for all materials and the manufacturing process, and shall perform visual inspection of the finished product. The approved agency shall place a distinguishing mark, and/or tag with this distinguishing mark, on each inspected joist or joist girder. This mark or tag shall remain on the joist or joist girder throughout the job site receiving and erection process.

1705.2.5 Cold-Formed Steel Trusses Spanning 60 Feet or Greater

Where a cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.

1705.2.5.1 Light-Framed Steel Truss Inspection and Testing

[OSHPD 1R, 2 & 5] Regardless of truss span, the manufacture of cold-formed light-framed steel trusses shall be continuously inspected by an approved agency. The approved agency shall verify conformance of materials and manufacture with approved construction documents. The approved agency shall place a distinguishing mark, and/or tag with this distinguishing mark, on each inspected truss. This mark or tag shall remain on the truss throughout the job site receiving and erection process. Refer to Section 2206.1.3.3 for requirements applicable to manufactured trusses specified therein.

1705.2.6 Metal Building Systems

Special inspections of metal building systems shall be performed in accordance with Sections 1705.2.1, 1705.2.3, 1705.2.4 and 1705.2.5 and Table 1705.2.6. The approved agency shall perform inspections of the erected metal building system to verify compliance with the approved construction documents.

TABLE 1705.2.6—SPECIAL INSPECTIONS OF METAL BUILDING SYSTEMS

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| --- | --- | --- |
| 1. Installation of rafter/beam flange braces and column flange braces. | — | X |
| 2. Installation of purlins and girts, including specified lapping. | — | X |
| 3. Purlin and girt restraint/bridging/bracing. | — | X |
| 4. Installation of X-bracing, tightened to remove any sag. | — | X |

1705.2.7 Special Inspection and Tests of Structural Welding

[OSHPD 1R, 2 & 5] Special inspections and testing (including nondestructive testing) of all shop and field welding operations shall be in accordance with this section and Sections 1705.2.1, 1705.2.2, 1705.13.1, and 1705.14.1, as applicable. Special inspections shall be performed by an approved welding inspector. The minimum requirements for a qualified welding special inspector shall be as those for an AWS Certified Welding Inspector (CWI), as defined in the provisions of the AWS QC1 or AWS B5.1.

The welding inspector shall make a systematic daily record of all welds. This record shall include:

- Identification marks of welders.

- List of defective welds.

- Manner of correction of defects.

The welding inspector shall check the material, details of construction and procedure, as well as workmanship of the welds. The special inspector shall verify that the installation of end-welded stud shear connectors are in accordance with the requirements of Section 2216.2 and the approved construction documents. The approved agency shall furnish the architect, structural engineer and the enforcement agency with a verified report that the welding has been done in conformance with AWS D1.1, D1.3, D1.4, D1.6, D1.8, and the approved construction documents.

1705.2.8 Special Inspection and Tests of High-Strength Fastener Assemblies

[OSHPD 1R, 2 & 5] Special inspections and tests for high-strength fasteners shall be in accordance with this section and Section 2216.1.

1705.3 Concrete Construction

Diagram

Special inspections and tests of concrete construction shall be performed in accordance with this section and Table 1705.3.

Exception: Special inspections and tests shall not be required for: [OSHPD 1R, 2 & 5] Exceptions 1 through 4 are not permitted by OSHPD.

- Isolated spread concrete footings of buildings three stories or less above grade plane that are fully supported on earth or rock.

- Continuous concrete footings supporting walls of buildings three stories or less above grade plane that are fully supported on earth or rock where:

  - The footings support walls of light-frame construction.

  - The footings are designed in accordance with Table 1809.7.

  - The structural design of the footing is based on a specified compressive strength, f'c, not more than 2,500 pounds per square inch (psi) (17.2 MPa), regardless of the compressive strength specified in the approved construction documents or used in the footing construction.

- Nonstructural concrete slabs supported directly on the ground, including prestressed slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 MPa).

- Concrete foundation walls constructed in accordance with Table 1807.1.6.2.

- Concrete patios, driveways and sidewalks, on grade.

TABLE 1705.3—REQUIRED SPECIAL INSPECTIONS AND TESTS OF CONCRETE CONSTRUCTION

|  | TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARDa | CBC REFERENCE |
| --- | --- | --- | --- | --- | --- |
| 1. | Inspect reinforcement, including prestressing tendons, and verify placement. | — | X | ACI 318: Ch. 20, 25.2, 25.3, 26.6.1-26.6.3 | — |
| 2. | Reinforcing bar welding: |  |  |  | — |
|  | a. Verify weldability of reinforcing bars other than ASTM A706. | — | X | AWS D1.4 ACI 318: 26.13.1.4 |  |
|  | b. Inspect welding of reinforcement for special moment frames, boundary elements of special structural walls and coupling beams. | X | — | AWS D1.4 ACI 318: 26.13.3 |  |
|  | c. Inspect welded reinforcement splices. | X | — | — |  |
|  | d. Inspect welding of primary tension reinforcement in corbels. | X | — | — |  |
|  | e. Inspect single-pass fillet welds, maximum 5/16". | — | X | AWS D1.4 ACI 318: 26.13.3 |  |
|  | f. Inspect all other welds. | — | X | AWS D1.4 ACI 318: 26.13.3 |  |
| 3. | Inspect anchors cast in concrete. | — | X | ACI 318: 26.13.3.3 | — |
| 4. | Inspect anchors post-installed in hardened concrete members:b |  |  |  | — |
|  | a. Adhesive anchors installed in horizontally or upwardly inclined orientations to resist sustained tension loads.c | X | — | ACI 318: 26.13.3.2 |  |
|  | b. Mechanical anchors and adhesive anchors not defined in 4.a. | — | X | ACI 318: 26.13.3 |  |
| 5. | Verify use of required design mix. | — | X | ACI 318: Ch. 19, 26.4.3, 26.4.4 | 1904.1, 1904.2 |
| 6. | Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. | X | — | ASTM C31 ASTM C172 ACI 318: 26.5, 26.12 | — |
| 7. | Inspect concrete and shotcrete placement for proper application techniques. | X | — | ACI 318: 26.5 | — |
| 8. | Verify maintenance of specified curing temperature and techniques. | — | X | ACI 318: 26.5.3-26.5.5 | — |
| 9. | Inspect prestressed concrete for: |  |  |  | — |
|  | a. Application of prestressing forces. | X | — | ACI 318: 26.10 |  |
|  | b. Grouting of bonded prestressing tendons. | X | — |  |  |
| 10. | Inspect erection of precast concrete members. | — | X | ACI 318: 26.9 | — |
| 11. | For precast concrete diaphragm connections or reinforcement at joints classified as moderate or high deformability elements (MDE or HDE) in structures assigned to Seismic Design Category C, D, E or F, inspect such connections and reinforcement in the field for: |  |  | ACI 318: 26.13.1.3 ACI 550.5 | — |
|  | a. Installation of the embedded parts. | X | — |  |  |
|  | b. Completion of the continuity of reinforcement across joints. | X | — |  |  |
|  | c. Completion of connections in the field. | X | — |  |  |
| 12. | Inspect installation tolerances of precast concrete diaphragm connections for compliance with ACI 550.5. | — | X | ACI 318: 26.13.1.3 | — |
| 13. | Verify in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | — | X | ACI 318: 26.11.2 | — |
| 14. | Inspect formwork for shape, location and dimensions of the concrete member being formed. | — | X | ACI 318: 26.11.1.2(b) | — |

For SI: 1 inch = 25.4 mm.

- Where applicable, see Section 1705.13.

- Specific requirements for special inspection shall be included in the research report for the anchor issued by an approved source in accordance with 26.13 in ACI 318, or other qualification procedures. Where specific requirements are not provided, special inspection requirements shall be specified by the registered design professional and shall be approved by the building official prior to the commencement of the work.

- [OSHPD 1R, 2 & 5] Installation of all adhesive anchors in horizontal and upwardly inclined positions shall be performed by an ACI/CRSI Certified Adhesive Anchor Installer, except where the factored design tension on the anchors is less than 100 pounds and those anchors are clearly noted on the approved construction documents or where the anchors are shear dowels across cold joints in slabs on grade where the slab is not part of the lateral force-resisting system.

UpCodes Diagrams (5)

Typical Distributed Tendon Profile - Slab

Example: Interior Wall Footing

Example: Interior Steel Column to Foundation

Example: Profile for Reversed Parabola Tendons

Example: Profile for Partial Parabola Tendons

1705.3.1 Welding of Reinforcing Bars

Special inspections of welding and qualifications of special inspectors for reinforcing bars shall be in accordance with the requirements of AWS D1.4 for special inspection and of AWS D1.4 for special inspector qualification.

1705.3.2 Material Tests

In the absence of sufficient data or documentation providing evidence of conformance to quality standards for materials in Chapters 19 and 20 of ACI 318, the building official shall require testing of materials in accordance with the appropriate standards and criteria for the material in Chapters 19 and 20 of ACI 318.

1705.3.3 Batch Plant Inspection

[OSHPD 1R, 2 & 5] Except as provided under this section, the quality and quantity of materials used in transit-mixed concrete and in batched aggregates shall be continuously inspected by an approved agency at the location where materials are measured.

1705.3.3.1 Waiver of Continuous Batch Plant Inspection

Continuous batch plant inspection shall be permitted to be waived by the registered design professional, subject to approval by the enforcement agency under either of the following conditions:

- The concrete plant complies fully with the requirements of ASTM C94, Sections 9 and 10, and has a current certificate from the National Ready Mixed Concrete Association or another agency acceptable to the enforcement agency. The certification shall indicate that the plant has automatic batching and recording capabilities.

- For single-story light-framed construction (without basement or retaining walls higher than 6 feet in height measured from bottom of footing to top of wall) and isolated foundations supporting equipment only, where deep foundation elements are not used.

When continuous batch plant inspection is waived, the following requirements shall apply and shall be described in the construction documents:

- An approved agency shall check the first batch at the start of the day to verify materials and proportions conform to the approved mix design.

- A licensed weighmaster shall positively identify quantity of materials and certify each load by a batch ticket.

- Batch tickets, including material quantities and weights, shall accompany the load, shall be transmitted to the inspector of record by the truck driver with load identified thereon. The load shall not be placed without a batch ticket identifying the mix. The inspector of record shall keep a daily record of placements, identifying each truck, its load, time of receipt at the job site and approximate location of deposit in the structure and shall maintain a copy of the daily record as required by the enforcement agency.

1705.3.4 Inspection and Testing of Prestressed Concrete

[OSHPD 1R, 2 & 5] Inspections and tests for prestressed concrete work shall be in accordance with this section. Tests for prestressing steel and anchorage shall be in accordance with Section 1910A.3. Inspection shall be in accordance with the following:

- In addition to the general inspection required for concrete work, all plant fabrication of prestressed concrete members or tensioning of post-tensioned members constructed at the site shall be continuously inspected by an approved special inspector.

Exception: The special inspector need not be continuously present for the placement of prestress or post-tensioned cables or tendons.

- The prestressed concrete plant fabrication special inspector shall check the materials, equipment, tensioning procedure and construction of the prestressed members and prepare daily written reports. The approved agency shall make a verified report identifying the members by mark and shall include such pertinent data as lot numbers of tendons used, tendon jacking forces, age and strength of concrete at time of tendon release and such other information that may be required.

- The special inspector of prestressed members post-tensioned at the site shall check the condition of the prestressing tendons, anchorage assemblies and concrete in the area of the anchorage, the tensioning equipment and the tensioning procedure and prepare daily written reports. The approved agency shall make a verified report of the prestressing operation identifying the members or tendons by mark and including such pertinent data as the initial cable slack, net elongation of tendons, jacking force developed and such other information as may be required.

- The verified reports of construction shall show that of the special inspector's own personal knowledge, the work covered by the report has been performed and materials used and installed in every material respect in compliance with the duly approved construction documents for plant fabrication inspection. The verified report shall be accompanied by test reports required for materials used. For site post-tensioning special inspections, the verified report shall be accompanied by copies of calibration charts, certified by an approved testing laboratory, showing the relationship between gage readings and force applied by the jacks used in the prestressing procedure

1705.3.5 Concrete Pre-Placement Inspection

[OSHPD 1R, 2 & 5] Concrete shall not be placed until the forms and reinforcement have been inspected, all preparations for the placement have been completed, and the preparations have been checked by the Inspector of Record.

1705.3.6 Placing Record

[OSHPD 1R, 2 & 5] A record shall be kept on the site of the time and date of placing the concrete in each portion of the structure. Such record shall be kept until the completion of the structure and shall be open to the inspection of the enforcement agency.

1705.3.7 Composite Construction Cores

[OSHPD 1R, 2 & 5] Composite construction cores shall be taken and tested in accordance with Section 1910A.4.

1705.3.8 Special Inspections and Tests for Post-Installed Anchors in Concrete

[OSHPD 1R, 2 & 5] Special inspections and tests for post-installed anchors in concrete shall be in accordance with Table 1705.3 and Section 1901.3.

1705.3.9 Shotcrete

[OSHPD 1R, 2 & 5] All shotcrete work shall be continuously inspected during placing by an approved agency. The shotcrete special inspector shall check the materials, placing equipment, details of construction and construction procedure. The approved agency shall furnish a verified report that of his or her own personal knowledge the work covered by the report has been performed and materials have been used and installed in every material respect in compliance with the duly approved construction documents.

1705.3.9.1 Visual Examination for Structural Soundness of In-Place Shotcrete

Completed shotcrete work shall be checked visually for reinforcing bar embedment, voids, rock pockets, sand streaks and similar deficiencies by examining a minimum of three 3-inch (76 mm) cores taken from three areas chosen by the design engineer which represent the worst congestion of reinforcing bars occurring in the project. Extra reinforcing bars may be added to noncongested areas and cores may be taken from these areas. The cores shall be examined by the special inspector and a report submitted to the enforcement agency prior to final approval of the shotcrete.

Exception: Shotcrete work fully supported on earth, minor repairs, and when, in the opinion of the enforcement agency, no special hazard exists.

1705.3.9.2 Preconstruction Tests

A shotcrete mockup panel shall be shot, cured, cored or sawn, examined and tested prior to commencement of the project. The mockup panel shall be representative of the project and simulate job conditions as closely as possible. The mockup panel thickness and reinforcing shall reproduce the thickest and most congested area specified in the structural design. It shall be shot at the same angle, using the same nozzleman and with the same concrete mix design that will be used on the project. Adequate encasement of bars larger than No. 5 shall be demonstrated by the mockup panels. The equipment used in preconstruction testing shall be the same equipment used in the work requiring such testing, unless substitute equipment is approved by the building official. Reports of preconstruction tests shall be submitted to the building official as specified in Section 1704.5.

1705.4 Masonry Construction

Special inspections and tests of masonry construction shall be performed in accordance with the quality assurance program requirements of TMS 402 and TMS 602. [OSHPD 1R, 2 & 5] as set forth in Tables 3 and 4, Level 3 requirements and Chapter 21. Testing shall be performed in accordance with Section 2105. Special inspection and testing of post-installed anchors in masonry shall be required in accordance with requirements for concrete in Chapters 17 and 19. Batch plant inspection of grout materials shall be in accordance with Section 1705.3.3.

Exception: [OSHPD 1R, 2 & 5] Not permitted by OSHPD. Special inspections and tests shall not be required for:

- Glass unit masonry or masonry veneer designed in accordance with Section 2110 or Chapter 14, respectively, where they are part of a structure classified as Risk Category I, II or III.

- Masonry foundation walls constructed in accordance with Table 1807.1.6.3(1), 1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4).

- Masonry fireplaces, masonry heaters or masonry chimneys installed or constructed in accordance with Section 2111, 2112 or 2113, respectively.

Building products (11)

Atlas® 10 x 2¼ x 16

Interstate Brick

Atlas® 10 x 4 x 16

Interstate Brick

Atlas® 6 x 2¼ x 12

Interstate Brick

Atlas® 6 x 2¼ x 16

Interstate Brick

Atlas® 6 x 4 x 16

Interstate Brick

Atlas® 8 x 2¼ x 16

Interstate Brick

Atlas® 8 x 4 x 12

Interstate Brick

Atlas® 8 x 4 x 16

Interstate Brick

Atlas® Emperor 4 x 4 x 16

Interstate Brick

Atlas® Utility 4 x 4 x 12

Interstate Brick

Super Atlas® 8 x 8 x16

Interstate Brick

1705.4.1 Glass Unit Masonry and Masonry Veneer in Risk Category IV

Special inspections and tests for glass unit masonry or masonry veneer designed in accordance with Section 2110 or Chapter 14, respectively, where they are part of a structure classified as Risk Category IV shall be performed in accordance with TMS 602 Level 2. [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

[OSHPD 1R, 2 & 5] Glass unit masonry and masonry veneer in Risk Category II, III or IV. Special inspections and tests for glass unit masonry or masonry veneer designed by Section 2110 or Chapter 14, respectively, in structures classified as Risk Category II, III or IV, shall be performed in accordance with TMS 602 Tables 3 and 4, Level 2 Quality Assurance.

1705.4.1.1 TMS 602 Section 1.6 Quality Assurance

[OSHPD 1R, 2 & 5] Replace footnote (d) as follows: (d) Periodic special inspection is required for all veneer.

1705.4.2 Vertical Masonry Foundation Elements

Special inspections and tests of vertical masonry foundation elements shall be performed in accordance with Section 1705.4.

1705.5 Wood Construction

Special inspections of prefabricated wood structural elements and assemblies shall be in accordance with Section 1704.2.5. Special inspections of site-built assemblies shall be in accordance with this section.

1705.5.1 High-Load Diaphragms

High-load diaphragms designed in accordance with Section 2306.2 shall be installed with special inspections as indicated in Section 1704.2. The special inspector shall inspect the wood structural panel sheathing to ascertain whether it is of the grade and thickness shown on the approved construction documents. Additionally, the special inspector must verify the nominal size of framing members at adjoining panel edges, the nail or staple diameter and length, the number of fastener lines and that the spacing between fasteners in each line and at edge margins agrees with the approved construction documents.

1705.5.2 Metal-Plate-Connected Wood Trusses Spanning 60 Feet or Greater

Where a truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.

1705.5.3 Mass Timber Construction

Special inspections of mass timber elements in Types IV-A, IV-B and IV-C construction shall be in accordance with Table 1705.5.3.

TABLE 1705.5.3—REQUIRED SPECIAL INSPECTIONS OF MASS TIMBER CONSTRUCTION

| TYPE |  |  | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| --- | --- | --- | --- | --- |
| 1. | Inspection of anchorage and connections of mass timber construction to timber deep foundation systems. |  | — | X |
| 2. | Inspect erection of mass timber construction. |  | — | X |
| 3. | Inspection of connections where installation methods are required to meet design loads. |  |  |  |
|  | Threaded fasteners. | Verify use of proper installation equipment. | — | X |
|  |  | Verify use of pre-drilled holes where required. | — | X |
|  |  | Inspect screws, including diameter, length, head type, spacing, installation angle and depth. | — | X |
|  | Adhesive anchors installed in horizontal or upwardly inclined orientation to resist sustained tension loads. |  | X | — |
|  | Adhesive anchors not defined in preceding cell. |  | — | X |
|  | Bolted connections. |  | — | X |
|  | Concealed connections. |  | — | X |

1705.5.4 Manufactured Trusses and Assemblies

[OSHPD 1R, 2 & 5] The fabrication of trusses and other assemblages constructed using wood and metal members, or using light metal plate connectors, shall be continuously inspected by an approved agency. The approved agency shall furnish the architect, structural engineer and the enforcement agency with a report that the lumber species, grades and moisture content; type of glue, temperature and gluing procedure; type of metal members and metal plate connectors; and the workmanship conform in every material respect with the duly approved construction documents. Each inspected truss shall be stamped by the approved agency with an identifying mark.

1705.5.5 Structural Glued Laminated and Cross-Laminated Timber

[OSHPD 1R, 2 & 5] Manufacture of all structural glued laminated and cross-laminated timber shall be continuously inspected by an approved agency.

The approved agency shall verify that proper quality control procedures and tests have been employed for all materials and the manufacturing process, and shall perform visual inspection of the finished product. Each inspected member shall be stamped by the approved agency with an identification mark.

Exception: Special Inspection is not required for non-custom prismatic glued laminated members identified on drawings and sourced from stock or general inventory of 51/2-inch (140 mm) maximum width and 18-inch (457 mm) maximum depth, and with a maximum clear span of 32 feet (9754 mm), manufactured and marked in accordance with ANSI /APA A190.1 Section 14.1 for noncustom members.

1705.5.6 Manufactured Open Web Trusses

[OSHPD 1R, 2 & 5] The manufacture of open web trusses shall be continuously inspected by an approved agency.

The approved agency shall verify that proper quality control procedures and tests have been employed for all materials and the manufacturing process, and shall perform visual inspection of the finished product. Each inspected truss shall be stamped with an identification mark by the approved agency.

1705.5.7 Timber Connectors

[OSHPD 1R, 2 & 5] The installation of all split ring and shear plate timber connectors and timber rivets shall be continuously inspected by an approved agency. The approved agency shall furnish the architect, structural engineer and the enforcement agency with a report verifying that the materials, timber connectors and workmanship conform to the approved construction documents.

1705.6 Soils

Special inspections and tests of existing site soil conditions, fill placement and load-bearing requirements shall be performed in accordance with this section and Table 1705.6. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance.

Exception: Where Section 1803 does not require reporting of materials and procedures for fill placement, the special inspector shall verify that the in-place dry density of the compacted fill is not less than 90 percent of the maximum dry density at optimum moisture content determined in accordance with ASTM D1557.

TABLE 1705.6—REQUIRED SPECIAL INSPECTIONS AND TESTS OF SOILS

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| --- | --- | --- |
| 1. Verify materials below shallow foundations are adequate to achieve the design bearing capacity. | — | X |
| 2. Verify excavations are extended to proper depth and have reached proper material. | — | X |
| 3. Perform classification and testing of compacted fill materials. | — | X |
| 4. During fill placement, verify use of proper materials and procedures in accordance with the provisions of the approved geotechnical report. Verify densities and lift thicknesses during placement and compaction of compacted fill. | X | — |
| 5. Prior to placement of compacted fill, inspect subgrade and verify that site has been prepared properly. | — | X |

1705.6.1 Soil Fill

[OSHPD 1R, 2 & 5] All fills used to support the foundations of any building or structure shall be continuously inspected by the geotechnical engineer or his or her qualified representative. It shall be the responsibility of the geotechnical engineer to verify that fills meet the requirements of the approved construction documents and to coordinate all fill inspection and testing during construction involving such fills.

The duties of the geotechnical engineer or his or her qualified representative shall include, but need not be limited to, the inspection of cleared areas and benches prepared to receive fill; inspection of the removal of all unsuitable soils and other materials; the approval of soils to be used as fill material; the inspection of placement and compaction of fill materials; the testing of the completed fills; and the inspection or review of geotechnical drainage devices, buttress fills or other similar protective measures in accordance with the approved construction documents.

A verified report shall be submitted by the geotechnical engineer as required by the California Administrative Code. The report shall indicate that all tests and inspections required by the approved construction documents were completed and whether the tested materials and/or inspected work meet the requirements of the approved construction documents.

1705.7 Driven Deep Foundations

Special inspections and tests shall be performed during installation of driven deep foundation elements as specified in Table 1705.7. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance.

TABLE 1705.7—REQUIRED SPECIAL INSPECTIONS AND TESTS OF DRIVEN DEEP FOUNDATION ELEMENTS

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| --- | --- | --- |
| 1. Verify element materials, sizes and lengths comply with the requirements. | X | — |
| 2. Determine capacities of test elements and conduct additional load tests, as required. | X | — |
| 3. Inspect driving operations and maintain complete and accurate records for each element. | X | — |
| 4. Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element. | X | — |
| 5. For steel elements, perform additional special inspections in accordance with Section 1705.2. | In accordance with Section 1705.2 |  |
| 6. For concrete elements and concrete-filled elements, perform tests and additional special inspections in accordance with Section 1705.3. | In accordance with Section 1705.3 |  |
| 7. For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge. | In accordance with Statement of Special Inspections |  |

1705.7.1 Driven Deep Foundations Observation

[OSHPD 1R, 2 & 5] The installation of driven deep foundations shall be continuously observed by a qualified representative of the geotechnical engineer responsible for that portion of the project.

The representative of the geotechnical engineer shall make a report of the deep foundation pile-driving operation giving such pertinent data as the physical characteristics of the deep foundation pile-driving equipment, identifying marks for each deep foundation pile, total depth of embedment for each deep foundation; and when the allowable deep foundation pile loads are determined by a dynamic load formula, the design formula used, and the permanent penetration under the last 10 blows. One copy of the report shall be sent to the enforcement agency.

1705.8 Cast-in-Place Deep Foundations

Special inspections and tests shall be performed during installation of cast-in-place deep foundation elements as specified in Table 1705.8. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance.

TABLE 1705.8—REQUIRED SPECIAL INSPECTIONS AND TESTS OF CAST-IN-PLACE DEEP FOUNDATION ELEMENTS

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| --- | --- | --- |
| 1. Inspect drilling operations and maintain complete and accurate records for each element. | X | — |
| 2. Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete or grout volumes. | X | — |
| 3. For concrete elements, perform tests and additional special inspections in accordance with Section 1705.3. | In accordance with Section 1705.3 |  |

1705.9 Helical Pile Foundations

Continuous special inspections shall be performed during installation of helical pile foundations. The information recorded shall include installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the registered design professional in responsible charge. The approved geotechnical report and the construction documents prepared by the registered design professional shall be used to determine compliance.

1705.10 Structural Integrity of Deep Foundation Elements

Whenever there is a reasonable doubt as to the structural integrity of a deep foundation element, an engineering assessment shall be required. The engineering assessment shall include tests for defects performed in accordance with ASTM D4945, ASTM D5882, ASTM D6760 or ASTM D7949, or other approved method.

1705.11 Fabricated Items

Special inspections of fabricated items shall be performed in accordance with Section 1704.2.5.

1705.12 Special Inspections for Wind Resistance

Special inspections for wind resistance specified in Sections 1705.12.1 through 1705.12.3, unless exempted by the exceptions to Section 1704.2, are required for buildings and structures constructed in the following areas:

- In wind Exposure Category B, where basic wind speed, V, is 150 mph (67 m/sec) or greater.

- In wind Exposure Category C or D, where basic wind speed, V, is 140 mph (62.6 m/sec) or greater.

1705.12.1 Structural Wood

Continuous special inspection is required during field gluing operations of elements of the main windforce-resisting system. Periodic special inspection is required for nailing, bolting, anchoring and other fastening of elements of the main windforce-resisting system, including wood shear walls, wood diaphragms, drag struts, braces and hold-downs.

Exception: Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the main windforce-resisting system, where the lateral resistance is provided by structural sheathing and the specified fastener spacing at panel edges is more than 4 inches (102 mm) on center.

1705.12.2 Cold-Formed Steel Light-Frame Construction

Periodic special inspection is required for welding operations of elements of the main windforce-resisting system. Periodic special inspection is required for screw attachment, bolting, anchoring and other fastening of elements of the main windforce-resisting system, including shear walls, braces, diaphragms, collectors (drag struts) and hold-downs.

Exception: Special inspections are not required for cold-formed steel light-frame shear walls and diaphragms, including screwing, bolting, anchoring and other fastening to components of the windforce-resisting system, where either of the following applies:

- The sheathing is gypsum board or fiberboard.

- The sheathing is wood structural panel or steel sheets on only one side of the shear wall, shear panel or diaphragm assembly and the specified fastener spacing at the panel or sheet edges is more than 4 inches (102 mm) on center (o.c.).

1705.12.3 Wind-Resisting Components

Periodic special inspection is required for fastening of the following systems and components:

- Roof covering, roof deck and roof framing connections.

- Exterior wall covering and wall connections to roof and floor diaphragms and framing.

1705.13 Special Inspections for Seismic Resistance

Special inspections for seismic resistance shall be required as specified in Sections 1705.13.1 through 1705.13.9, unless exempted by the exceptions of Section 1704.2.

Exception: The special inspections specified in Sections 1705.13.1 through 1705.13.9 are not required for structures designed and constructed in accordance with one of the following:

- The structure consists of light-frame construction; the design spectral response acceleration at short periods, SDS, as determined in Section 1613.2.4, does not exceed 0.5; and the building height of the structure does not exceed 35 feet (10 668 mm).

- The seismic force-resisting system of the structure consists of reinforced masonry or reinforced concrete; the design spectral response acceleration at short periods, SDS, as determined in Section 1613.2.4, does not exceed 0.5; and the building height of the structure does not exceed 25 feet (7620 mm).

- The structure is a detached one- or two-family dwelling not exceeding two stories above grade plane and does not have any of the following horizontal or vertical irregularities in accordance with Section 12.3 of ASCE 7:

  - Torsional or extreme torsional irregularity.

  - Nonparallel systems irregularity.

  - Stiffness-soft story or stiffness-extreme soft story irregularity.

  - Discontinuity in lateral strength-weak story irregularity.

1705.13.1 Structural Steel

Special inspections for seismic resistance shall be in accordance with Section 1705.13.1.1 or 1705.13.1.2, as applicable.

1705.13.1.1 Seismic Force-Resisting Systems

Special inspections of structural steel in the seismic force-resisting systems in buildings and structures assigned to Seismic Design Category B, C, D, E or F shall be performed in accordance with the quality assurance requirements of AISC 341. [OSHPD 1R, 2 & 5] and this code.

Exceptions: [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- In buildings and structures assigned to Seismic Design Category B or C, special inspections are not required for structural steel seismic force-resisting systems where the response modification coefficient, R, designated for "Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems" in ASCE 7, Table 12.2-1, has been used for design and detailing.

- In structures assigned to Seismic Design Category D, E, or F, special inspections are not required for structural steel seismic force-resisting systems where design and detailing in accordance with AISC 360 is permitted by ASCE 7, Table 15.4-1.

1705.13.1.2 Structural Steel Elements

Special inspections of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, D, E or F other than those covered in Section 1705.13.1.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. [OSHPD 1R, 2 & 5] and this code.

Exceptions: [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- In buildings and structures assigned to Seismic Design Category B or C, special inspections of structural steel elements are not required for seismic force-resisting systems with a response modification coefficient, R, of 3 or less.

- In structures assigned to Seismic Design Category D, E, or F, special inspections of structural steel elements are not required for seismic force-resisting systems where design and detailing other than AISC 341 is permitted by ASCE 7, Table 15.4-1. Special inspection shall be in accordance with the applicable referenced standard listed in ASCE 7, Table 15.4-1.

1705.13.2 Structural Wood

For the seismic force-resisting systems of structures assigned to Seismic Design Category C, D, E or F:

- Continuous special inspection shall be required during field gluing operations of elements of the seismic force-resisting system.

- Periodic special inspection shall be required for nailing, bolting, anchoring and other fastening of elements of the seismic force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, shear panels and hold-downs.

Exception: Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the seismic force-resisting system, where the lateral resistance is provided by structural sheathing, and the specified fastener spacing at the panel edges is more than 4 inches (102 mm) on center.

1705.13.3 Cold-Formed Steel Light-Frame Construction

For the seismic force-resisting systems of structures assigned to Seismic Design Category C, D, E or F, periodic special inspection shall be required for both:

- Welding operations of elements of the seismic force-resisting system.

- Screw attachment, bolting, anchoring and other fastening of elements of the seismic force-resisting system, including shear walls, braces, diaphragms, collectors (drag struts) and hold-downs.

Exception: Special inspections are not required for cold-formed steel light-frame shear walls and diaphragms, including screw installation, bolting, anchoring and other fastening to components of the seismic force-resisting system, where either of the following applies:

- The sheathing is gypsum board or fiberboard.

- The sheathing is wood structural panel or steel sheets on only one side of the shear wall, shear panel or diaphragm assembly and the specified fastener spacing at the panel or sheet edge is more than 4 inches (102 mm) on center.

1705.13.4 Designated Seismic Systems

For structures assigned to Seismic Design Category C, D, E or F, the special inspector shall examine designated seismic systems requiring seismic qualification in accordance with Section 13.2.3 of ASCE 7 and verify that the label, anchorage and mounting conform to the certificate of compliance.

1705.13.5 Architectural Components

Periodic special inspection is required for the erection and fastening of exterior cladding, interior and exterior nonbearing walls and interior and exterior veneer in structures assigned to Seismic Design Category D, E or F.

Exception: Periodic special inspection is not required for the following:

- Exterior cladding, interior and exterior nonbearing walls and interior and exterior veneer 30 feet (9144 mm) or less in height above grade or walking surface.

- Exterior cladding and interior and exterior veneer weighing 5 psf (0.24 kN/m2) or less.

- Interior nonbearing walls weighing 15 psf (0.72 kN/m2) or less.

1705.13.5.1 Access Floors

Periodic special inspection is required for the anchorage of access floors in structures assigned to Seismic Design Category D, E or F.

1705.13.6 Plumbing, Mechanical and Electrical Components

Diagram

Periodic special inspection of plumbing, mechanical and electrical components shall be required for the following:

- Anchorage of electrical equipment for emergency and standby power systems in structures assigned to Seismic Design Category C, D, E or F.

- Anchorage of other electrical equipment in structures assigned to Seismic Design Category E or F.

- Installation and anchorage of piping systems designed to carry hazardous materials and their associated mechanical units in structures assigned to Seismic Design Category C, D, E or F.

- Installation and anchorage of ductwork designed to carry hazardous materials in structures assigned to Seismic Design Category C, D, E or F.

- Installation and anchorage of vibration isolation systems in structures assigned to Seismic Design Category C, D, E or F where the approved construction documents require a nominal clearance of 1/4 inch (6.4 mm) or less between the equipment support frame and restraint.

- Installation of mechanical and electrical equipment, including duct work, piping systems and their structural supports, where automatic sprinkler systems are installed in structures assigned to Seismic Design Category C, D, E or F to verify one of the following:

  - Minimum clearances have been provided as required by Section 13.2.4 ASCE/SEI 7.

  - A nominal clearance of not less than 3 inches (76 mm) has been be provided between automatic sprinkler system drops and sprigs and: structural members not used collectively or independently to support the sprinklers; equipment attached to the building structure; and other systems' piping.

    - Where flexible sprinkler hose fittings are used, special inspection of minimum clearances is not required.

UpCodes Diagrams (2)

Allowed Clearance at Open Equipment Doors (<1000V)

Clearances at Electrical Equipment

1705.13.7 Storage Racks

Steel storage racks and steel cantilevered storage racks that are 8 feet (2438 mm) in height or greater and assigned to Seismic Design Category D, E or F shall be provided with periodic special inspection as required by Table 1705.13.7.

TABLE 1705.13.7—REQUIRED INSPECTIONS OF STORAGE RACK SYSTEMS

| TYPE | CONTINUOUS INSPECTION | PERIODIC INSPECTION | REFERENCED STANDARD | IBC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Materials used, to verify compliance with one or more of the material test reports in accordance with the approved construction documents. | — | X | — | — |
| 2. Fabricated storage rack elements. | — | X | — | Section 1704.2.5 |
| 3. Storage rack anchorage installation. | — | X | ANSI/MH16.1 Section 7.3.2 | — |
| 4. Completed storage rack system, to indicate compliance with the approved construction documents. | — | X | — | — |

1705.13.8 Seismic Isolation Systems

Periodic special inspection shall be provided for seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, D, E or F during the fabrication and installation of isolator units and energy dissipation devices.

1705.13.9 Cold-Formed Steel Special Bolted Moment Frames

Periodic special inspection shall be provided for the installation of cold-formed steel special bolted moment frames in the seismic force-resisting systems of structures assigned to Seismic Design Category D, E or F.

1705.14 Testing for Seismic Resistance

Testing for seismic resistance shall be required as specified in Sections 1705.14.1 through 1705.14.4, unless exempted from special inspections by the exceptions of Section 1704.2.

1705.14.1 Structural Steel

Nondestructive testing for seismic resistance shall be in accordance with Section 1705.14.1.1 or 1705.14.1.2, as applicable.

1705.14.1.1 Seismic Force-Resisting Systems

Nondestructive testing of structural steel in the seismic force-resisting systems in buildings and structures assigned to Seismic Design Category B, C, D, E or F shall be performed in accordance with the quality assurance requirements of AISC 341. [OSHPD 1R, 2 & 5] and this code.

Exceptions: [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- In buildings and structures assigned to Seismic Design Category B or C, nondestructive testing is not required for structural steel seismic force-resisting systems where the response modification coefficient, R, designated for "Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems" in ASCE 7, Table 12.2-1, has been used for design and detailing.

- In structures assigned to Seismic Design Category D, E, or F, nondestructive testing is not required for structural steel seismic force-resisting systems where design and detailing in accordance with AISC 360 is permitted by ASCE 7, Table 15.4-1.

1705.14.1.2 Structural Steel Elements

Nondestructive testing of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, D, E or F other than those covered in Section 1705.14.1.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. [OSHPD 1R, 2 & 5] and this code.

Exceptions: [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

- In buildings and structures assigned to Seismic Design Category B or C, nondestructive testing of structural steel elements is not required for seismic force-resisting systems with a response modification coefficient, R, of 3 or less.

- In structures assigned to Seismic Design Category D, E or F, nondestructive testing of structural steel elements is not required for seismic force-resisting systems where design and detailing other than AISC 341 is permitted by ASCE 7, Table 15.4-1. Nondestructive testing of structural steel elements shall be in accordance with the applicable referenced standard listed in ASCE 7, Table 15.4-1.

1705.14.2 Nonstructural Components

For structures assigned to Seismic Design Category B, C, D, E or F, where the requirements of Section 13.2.1 of ASCE 7 for nonstructural components, supports or attachments are met by seismic qualification as specified in Item 2 therein, the registered design professional shall specify on the approved construction documents the requirements for seismic qualification by analysis, testing or experience data. Certificates of compliance for the seismic qualification shall be submitted to the building official as specified in Section 1704.5.

[OSHPD 1R, 2 & 5] Seismic sway bracing components satisfying requirements of ANSI/FM 1950, ANSI/ASHRAE 171, or using an alternative testing protocol approved by the building official shall be deemed to satisfy the requirements of this section.

Note: Deemed to comply provisions provide acceptable options to comply with the code but do not mandate their use. Alternative systems in accordance with Section 104.2.3 and the California Administrative Code Section 7-104 are always acceptable when approved by the building official.

1705.14.3 Designated Seismic Systems

For structures assigned to Seismic Design Category C, D, E or F and with designated seismic systems that are subject to the requirements of Section 13.2.4 of ASCE 7 for certification, the registered design professional shall specify on the approved construction documents the requirements to be met by analysis, testing or experience data as specified therein. Certificates of compliance documenting that the requirements are met shall be submitted to the building official as specified in Section 1704.5.

1705.14.3.1 Special Seismic Certification

[OSHPD 1R, 2 & 5] Special seismic certification shall be required in accordance with Section 1705A.14.3. for all of the following:

- Life-safety components, such as emergency and standby power systems, mechanical smoke removal systems and firesprinkler/fire protection systems.

- Medical, mechanical and electrical equipment and components required for life support for patients.

- On-site power resources (PVs, batteries, fuel cells, etc.) provided to replace, in whole or in part, the public or private electric utility service.

- [OSHPD 2] Alternate power systems including:

  - Generators.

  - UPS and batteries.

  - Renewable electrical generation and controlequipment.

  - Panelboards as defined in the California Electrical Code (CEC) Article 100.

  - Manual and automatic transfer switches.

  - Switchgear and switchboards.

1705.14.4 Seismic Isolation Systems

Seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, D, E or F shall be tested in accordance with Section 17.8 of ASCE 7.

[BF] 1705.15 Sprayed Fire-Resistive Materials (SFRM)

Special inspections and tests of sprayed fire-resistive materials (SFRM) applied to floor, roof and wall assemblies and structural members shall be performed in accordance with Sections 1705.15.1 through 1705.15.6. Special inspections shall be based on the fire-resistance design as designated in the approved construction documents. The tests set forth in this section shall be based on samplings from specific floor, roof and wall assemblies and structural members. Special inspections and tests shall be performed during construction with an additional visual inspection after the rough installation of electrical, automatic sprinkler systems, mechanical and plumbing systems and suspension systems for ceilings, and before concealment where applicable. The required sample size shall not exceed 110 percent of that specified by the referenced standards in Sections 1705.15.4.1 through 1705.15.4.9.

[BF] 1705.15.1 Physical and Visual Tests

The special inspections and tests shall include the following to demonstrate compliance with the listing and the fire-resistance rating:

- Condition of substrates.

- Thickness of application.

- Density in pounds per cubic foot (kg/m3).

- Bond strength adhesion/cohesion.

- Condition of finished application.

[BF] 1705.15.2 Structural Member Surface Conditions

The surfaces shall be prepared in accordance with the approved fire-resistance design and the written instructions of approved manufacturers. The prepared surface of structural members to be sprayed shall be inspected by the special inspector before the application of the SFRM.

[BF] 1705.15.3 Application

The substrate shall have a minimum ambient temperature before and after application as specified in the written instructions of approved manufacturers. The area for application shall be ventilated during and after application as required by the written instructions of approved manufacturers.

[BF] 1705.15.4 Thickness

Not more than 10 percent of the thickness measurements of the SFRM applied to floor, roof and wall assemblies and structural members shall be less than the thickness required by the approved fire-resistance design, and none shall be less than the minimum allowable thickness required by Section 1705.15.4.1.

[BF] 1705.15.4.1 Minimum Allowable Thickness

For design thicknesses 1 inch (25 mm) or greater, the minimum allowable individual thickness shall be the design thickness minus 1/4 inch (6.4 mm). For design thicknesses less than 1 inch (25 mm), the minimum allowable individual thickness shall be the design thickness minus 25 percent. Thickness shall be determined in accordance with ASTM E605. Samples of the SFRM shall be selected in accordance with Sections 1705.15.4.2 through 1705.15.4.9.

[BF] 1705.15.4.2 Floor, Roof and Wall Assemblies

The thickness of the SFRM applied to floor, roof and wall assemblies shall be determined in accordance with ASTM E605, making not less than four measurements for each 1,000 square feet (93 m2) of the sprayed area, or portion thereof, in each story.

[BF] 1705.15.4.3 Cellular Decks

Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. Not fewer than four measurements shall be made, located symmetrically within the square area.

[BF] 1705.15.4.4 Fluted Decks

Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. Not fewer than four measurements shall be made, located symmetrically within the square area, including one each of the following: valley, crest and sides. The average of the measurements shall be reported.

[BF] 1705.15.4.5 Structural Members

The thickness of the SFRM applied to structural members shall be determined in accordance with ASTM E605. Thickness testing shall be performed on not less than 25 percent of the structural members on each floor.

[BF] 1705.15.4.6 Beams and Girders

At beams and girders thickness measurements shall be made at nine locations around the beam or girder at each end of a 12-inch (305 mm) length.

[BF] 1705.15.4.7 Joists and Trusses

At joists and trusses, thickness measurements shall be made at seven locations around the joist or truss at each end of a 12-inch (305 mm) length.

[BF] 1705.15.4.8 Wide-Flanged Columns

At wide-flanged columns, thickness measurements shall be made at 12 locations around the column at each end of a 12-inch (305 mm) length.

[BF] 1705.15.4.9 Hollow Structural Section and Pipe Columns

At hollow structural section and pipe columns, thickness measurements shall be made at not fewer than four locations around the column at each end of a 12-inch (305 mm) length.

[BF] 1705.15.5 Density

The density of the SFRM shall be not less than the density specified in the approved fire-resistance design. Density of the SFRM shall be determined in accordance with ASTM E605. The test samples for determining the density of the SFRM shall be selected as follows:

- From each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232 m2) or portion thereof of the sprayed area in each story.

- From beams, girders, trusses and columns at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232 m2) of floor area or portion thereof in each story.

[BF] 1705.15.6 Bond Strength

The cohesive/adhesive bond strength of the cured SFRM applied to floor, roof and wall assemblies and structural members shall be not less than 150 pounds per square foot (psf) (7.18 kN/m2). The cohesive/adhesive bond strength shall be determined in accordance with the field test specified in ASTM E736 by testing in-place samples of the SFRM selected in accordance with Sections 1705.15.6.1 through 1705.15.6.3.

[BF] 1705.15.6.1 Floor, Roof and Wall Assemblies

The test samples for determining the cohesive/adhesive bond strength of the SFRM shall be selected from each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232 m2) of the sprayed area, or portion thereof, in each story.

[BF] 1705.15.6.2 Structural Members

The test samples for determining the cohesive/adhesive bond strength of the SFRM shall be selected from beams, girders, trusses, columns and other structural members at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232 m2) of floor area or portion thereof in each story.

[BF] 1705.15.6.3 Primer, Paint and Encapsulant Bond Tests

Bond tests to qualify a primer, paint or encapsulant shall be conducted where the SFRM is applied to a primed, painted or encapsulated surface for which acceptable bond-strength performance between these coatings and the SFRM has not been determined. A bonding agent approved by the SFRM manufacturer shall be applied to a primed, painted or encapsulated surface where the bond strengths are found to be less than required values.

[BF] 1705.16 Intumescent Fire-Resistive Materials

Special inspections and tests for intumescent fire-resistive materials applied to structural elements and decks shall be performed in accordance with AWCI 12-B. Special inspections and tests shall be based on the fire-resistance design as designated in the approved construction documents. Special inspections and tests shall be performed during construction. Additional visual inspection shall be performed after the rough installation and, where applicable, prior to the concealment of electrical, automatic sprinkler, mechanical and plumbing systems.

[BF] 1705.17 Exterior Insulation and Finish Systems (EIFS)

Assembly

Special inspections shall be required for all EIFS applications.

Exceptions:

- Special inspections shall not be required for EIFS applications installed over a water-resistive barrier with a means of draining moisture to the exterior.

- Special inspections shall not be required for EIFS applications installed over masonry or concrete walls.

Assemblies (2)

WP 8122: 1hr, Steel Studs, Polymer Mod. EIFS

WP 8123; 1hr Steel Studs, Polymer Based EIFS

[BF] 1705.17.1 Water-Resistive Barrier Coating

A water-resistive barrier coating complying with ASTM E2570 requires special inspection of the water-resistive barrier coating where installed over a sheathing substrate.

[BF] 1705.18 Fire-Resistant Penetrations and Joints

Diagram

In high-rise buildings, in buildings assigned to Risk Category III or IV, or in fire areas containing Group R occupancies with an occupant load greater than 250, special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems and perimeter fire containment systems that are tested and listed in accordance with Sections 714.4.1.2, 714.5.1.2, 715.3.1 and 715.4 shall be in accordance with Section 1705.18.1 or 1705.18.2.

[OSHPD 1R, 2 & 5] Buildings assigned to all Risk Categories shall be subject to special inspections for fire-resistant penetrations and joints.

UpCodes Diagrams (2)

High Rise Buildings

Voids at Curtain Wall Intersections

Building products (4)

Thermafiber® FireSpan FF

Owens Corning

Thermafiber® FireSpan®

Owens Corning

Thermafiber® Safing

Owens Corning

Thermafiber® Safing FF

Owens Corning

[BF] 1705.18.1 Penetration Firestops

Inspections of penetration firestop systems that are tested and listed in accordance with Sections 714.4.1.2 and 714.5.1.2 shall be conducted by an approved agency in accordance with ASTM E2174.

[BF] 1705.18.2 Fire-Resistant Joint Systems

Inspection of fire-resistant joint systems that are tested and listed in accordance with Sections 715.3.1 and 715.4 shall be conducted by an approved agency in accordance with ASTM E2393.

[F] 1705.19 Testing for Smoke Control

Smoke control systems shall be tested by a special inspector.

[F] 1705.19.1 Testing Scope

The test scope shall be as follows:

- During erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location.

- Prior to occupancy and after sufficient completion for the purposes of pressure difference testing, flow measurements and detection and control verification.

[F] 1705.19.2 Qualifications

Approved agencies for smoke control testing shall have expertise in fire protection engineering, mechanical engineering and certification as air balancers.

1705.20 Sealing of Mass Timber

Periodic special inspections of sealants or adhesives shall be conducted where sealant or adhesive required by Section 703.7 is applied to mass timber building elements as designated in the approved construction documents.

Section 1706 Design Strengths of Materials

1706.1 Conformance to Standards

The design strengths and permissible stresses of any structural material that are identified by a manufacturer's designation as to manufacture and grade by mill tests, or the strength and stress grade is otherwise confirmed to the satisfaction of the building official, shall conform to the specifications and methods of design of accepted engineering practice or the approved rules in the absence of applicable standards.

1706.2 New Materials

For materials that are not specifically provided for in this code, the design strengths and permissible stresses shall be established by tests as provided for in Section 1707.

Section 1707 Alternative Test Procedure

1707.1 General

In the absence of approved rules or other approved standards, the building official shall make, or cause to be made, the necessary tests and investigations; or the building official shall accept duly authenticated reports from approved agencies in respect to the quality and manner of use of new materials or assemblies as provided for in Section 104.2.3 or 1.8.7, as applicable. The cost of all tests and other investigations required under the provisions of this code shall be borne by the owner or the owner's authorized agent.

[BSC] In the absence of approved rules or other approved standards, the building official shall make, or cause to be made, the necessary tests and investigations; or the building official shall accept duly authenticated reports from approved agencies in respect to the quality and manner of use of new materials or assemblies as provided for in Section 1.2.1, Chapter 1, Division I. The cost of all tests and other investigations required under the provisions of this code shall be borne by the applicant.

Section 1708 In-Situ Load Tests

1708.1 General

Whenever there is a reasonable doubt as to the stability or load-bearing capacity of a completed building, structure or portion thereof for the expected loads, an engineering assessment shall be required. The engineering assessment shall involve either a structural analysis or an in-situ load test, or both. The structural analysis shall be based on actual material properties and other as-built conditions that affect stability or load-bearing capacity, and shall be conducted in accordance with the applicable design standard. The in-situ load tests shall be conducted in accordance with Section 1708.2. If the building, structure or portion thereof is found to have inadequate stability or load-bearing capacity for the expected loads, modifications to ensure structural adequacy or the removal of the inadequate construction shall be required.

1708.2 In-Situ Load Tests

In-situ load tests shall be conducted in accordance with Section 1708.2.1 or 1708.2.2 and shall be supervised by a registered design professional. The test shall simulate the applicable loading conditions specified in Chapter 16 as necessary to address the concerns regarding structural stability of the building, structure or portion thereof.

1708.2.1 Load Test Procedure Specified

Where a referenced material standard contains an applicable load test procedure and acceptance criteria, the test procedure and acceptance criteria in the standard shall apply. In the absence of specific load factors or acceptance criteria, the load factors and acceptance criteria in Section 1708.2.2 shall apply.

1708.2.2 Load Test Procedure Not Specified

In the absence of applicable load test procedures contained within a material standard referenced by this code or acceptance criteria for a specific material or method of construction, such existing structure shall be subjected to an approved test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components that are not a part of the seismic force-resisting system, at a minimum the test load shall be equal to the specified factored design loads. For materials such as wood that have strengths that are dependent on load duration, the test load shall be adjusted to account for the difference in load duration of the test compared to the expected duration of the design loads being considered. For statically loaded components, the test load shall be left in place for a period of 24 hours. For components that carry dynamic loads (for example, machine supports or fall arrest anchors), the load shall be left in place for a period consistent with the component's actual function. The structure shall be considered to have successfully met the test requirements where the following criteria are satisfied:

- Under the design load, the deflection shall not exceed the limitations specified in Section 1604.3.

- Within 24 hours after removal of the test load, the structure shall have recovered not less than 75 percent of the maximum deflection.

- During and immediately after the test, the structure shall not show evidence of failure.

Section 1709 Preconstruction Load Tests

1709.1 General

Where proposed construction is not capable of being designed by approved engineering analysis, or where proposed construction design method does not comply with the applicable material design standard, the system of construction or the structural unit and the connections shall be subjected to the tests prescribed in Section 1709. The building official shall accept certified reports of such tests conducted by an approved testing agency, provided that such tests meet the requirements of this code and approved procedures.

1709.2 Load Test Procedures Specified

Where specific load test procedures, load factors and acceptance criteria are included in the applicable referenced standards, such test procedures, load factors and acceptance criteria shall apply. In the absence of specific test procedures, load factors or acceptance criteria, the corresponding provisions in Section 1709.3 shall apply.

1709.3 Load Test Procedures Not Specified

Where load test procedures are not specified in the applicable referenced standards, the load-bearing and deformation capacity of structural components and assemblies shall be determined on the basis of a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components and assemblies that are not a part of the seismic force-resisting system, the test shall be as specified in Section 1709.3.1. Load tests shall simulate the applicable loading conditions specified in Chapter 16.

1709.3.1 Test Procedure

The test assembly shall be subjected to an increasing superimposed load equal to not less than two times the superimposed design load. The test load shall be left in place for a period of 24 hours. The tested assembly shall be considered to have successfully met the test requirements if the assembly recovers not less than 75 percent of the maximum deflection within 24 hours after the removal of the test load. The test assembly shall then be reloaded and subjected to an increasing superimposed load until either structural failure occurs or the superimposed load is equal to two and one-half times the load at which the deflection limitations specified in Section 1709.3.2 were reached, or the load is equal to two and one-half times the superimposed design load. In the case of structural components and assemblies for which deflection limitations are not specified in Section 1709.3.2, the test specimen shall be subjected to an increasing superimposed load until structural failure occurs or the load is equal to two and one-half times the desired superimposed design load. The allowable superimposed design load shall be taken as the least of:

- The load at the deflection limitation given in Section 1709.3.2.

- The failure load divided by 2.5.

- The maximum load applied divided by 2.5.

1709.3.2 Deflection

The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3.

1709.4 Wall and Partition Assemblies

Load-bearing wall and partition assemblies shall sustain the test load both with and without window framing. The test load shall include all design load components. Wall and partition assemblies shall be tested both with and without door and window framing.

1709.5 Exterior Window and Door Assemblies

The design pressure rating of exterior windows and doors in buildings shall be determined in accordance with Section 1709.5.1 or 1709.5.2. For exterior windows and doors tested in accordance with Section 1709.5.1 or 1709.5.2, required design wind pressures determined from ASCE 7 shall be permitted to be converted to allowable stress design by multiplying by 0.6.

Exception: Structural wind load design pressures for window or door assemblies other than the size tested in accordance with Section 1709.5.1 or 1709.5.2 shall be permitted to be different than the design value of the tested assembly, provided that such pressures are determined by accepted engineering analysis or validated by an additional test of the window or door assembly to the alternative allowable design pressure in accordance with Section 1709.5.2. Components of the alternate size assembly shall be the same as the tested or labeled assembly. Where engineering analysis is used, it shall be performed in accordance with the analysis procedures of AAMA 2502 or WDMA I.S. 11.

1709.5.1 Exterior Windows and Doors

Exterior windows and sliding doors shall be tested and labeled as conforming to AAMA/WDMA/CSA101/I.S.2/A440. The label shall state the name of the manufacturer, the approved labeling agency and the product designation as specified in AAMA/WDMA/CSA101/I.S.2/A440. Exterior side-hinged doors shall be tested and labeled as conforming to AAMA/WDMA/CSA101/I.S.2/A440 or comply with Section 1709.5.2. Products tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440 shall not be subject to the requirements of Sections 2403.2 and 2403.3.

1709.5.2 Exterior Windows and Door Assemblies Not Provided for in Section 1709.5.1

Exterior window and door assemblies shall be tested in accordance with ASTM E330. Exterior window and door assemblies containing glass shall comply with Section 2403. The design pressure for testing shall be calculated in accordance with Chapter 16. Each assembly shall be tested for 10 seconds at a load equal to 1.5 times the design pressure.

1709.5.2.1 Garage Doors and Rolling Doors

Garage doors and rolling doors shall be tested in accordance with either ASTM E330 or ANSI/DASMA 108, and shall meet the pass/fail criteria of ANSI/DASMA 108. Garage doors and rolling doors shall be labeled with a permanent label identifying the door manufacturer, the door model/series number, the positive and negative design wind pressure rating, the installation instruction drawing reference number, and the applicable test standard.

1709.5.3 Windborne Debris Protection

Protection of exterior glazed openings in buildings located in windborne debris regions shall be in accordance with Section 1609.2.

1709.5.3.1 Impact Protective Systems Testing and Labeling

Impact protective systems shall be tested for impact resistance by an approved independent laboratory for compliance with ASTM E1886 and ASTM E1996 and for design wind pressure for compliance with ASTM E330. Required design wind pressures shall be determined in accordance with ASCE 7, and for the purposes of this section, multiplied by 0.6 to convert to allowable stress design.

Impact protective systems shall have a permanent label applied in accordance with Section 1703.5.4, identifying the manufacturer, product designation, performance characteristics, and approved inspection agency.

Building product (1)

GPX® Hurricane

SaftiFirst

1709.6 Skylights and Sloped Glazing

Skylights and sloped glazing shall comply with the requirements of Chapter 24.

1709.7 Test Specimens

Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on representative samples of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency.

Section 1710 Off-Site Construction [OSHPD 1R, 2 & 5]

1710.1 General

This section applies to off-site construction and shall govern the requirements for planning, design, fabrication, assembly, inspection and regulatory compliance.

1710.2 Construction

In addition to other applicable requirements in this code, off-site construction shall be in accordance with ICC 1200, with the texts modified by Sections 1710.2.1 through 1710.2.2.

1710.2.1 ICC 1200 Section 301.4

Replace ICC 1200 Section 301.4 by the following:

301.4 Use of shipping containers repurposed as buildings and building components. Use of shipping containers repurposed as buildings and building components is not permitted by the California Building Code (CBC) Section 3115.

1710.2.2 ICC 1200 Section 503.1

Modify ICC 1200 Section 503.1 by adding the following:

Quality Assurance/Quality Control (QA/QC) shall satisfy all the requirements for Testing, Inspection, and Observation (TIO) in the California Building Standards Code (CBSC).

1710.3 Regulatory Compliance

In addition to other applicable requirements in this code, off-site construction shall be inspected and regulated in accordance with ICC 1205, with texts modified by Sections 1710.3.1 through 1710.3.2.

1710.3.1 ICC 1205 Section 302.1

Modify ICC 1205 Section 302.1 by adding the following:

Construction documents for plan approval shall satisfy all the requirements in the California Building Standards Code (CBSC).

1710.3.2 ICC 1205 Section 501.1

Modify ICC 1205 Section 501.1 by adding the following:

Testing, Inspection, and Observation (TIO) program shall satisfy all the requirements in the California Building Standards Code (CBSC).