Chapter 18 Soils and Foundations

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE
CHAPTER 18 — SOILS AND FOUNDATIONS

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC- CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter | X |  |  |  |  |  |  |  |  |  |  |  | X |  |  | X |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) |  |  |  | X | X |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1801.1.1 — 1801.1.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1802.1 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1803.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1803.1.1 — 1803.1.1.5 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1803.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1803.3.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1803.6 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1803.7 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1804.4.1 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1805.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1805.4.1 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1807.1.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1807.1.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1807.1.5 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1807.1.6 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1807.2.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1808.8 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| Table 1808.8.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1808.8.6 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.7 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.8 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.9 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.12 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1809.15 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.1.5.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.2.4 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.3.1.9 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.5.3.3 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.8 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.10.4 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1810.3.10.4.1 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.11 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.3.11.2 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1810.4.1.5 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |
| 1811 — 1813 |  |  |  |  |  |  |  |  |  |  | X | X |  |  | X |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 18 provides criteria for geotechnical and structural considerations in the selection, design and installation of foundation systems to support the loads imposed by the structure above. This chapter includes requirements for soils investigation and site preparation for receiving a foundation, including the load-bearing values for soils and protection for the foundation from frost and water intrusion. Section 1808 addresses the basic requirements for all foundation types while subsequent sections address foundation requirements that are specific to shallow foundations and deep foundations.

ICC code development note: Code change proposals to this chapter will be considered by the IBC—Structural Code Development Committee during the 2025 (Group B) Code Development Cycle.

Section 1801 General

1801.1 Scope

The provisions of this chapter shall apply to building and foundation systems.

1801.1.1 Application

[OSHPD 1R, 2 & 5] The scope of application of Chapter 18 is as follows:

Structures regulated by the Department of Health Care Access and Information/Office of Statewide Hospital Planning and Development (OSHPD), which include hospital buildings removed from general acute care service, skilled nursing facility buildings, intermediate care facility buildings and acute psychiatric hospital buildings, as listed in Sections 1.10.1, 1.10.2 and 1.10.5.

1801.1.2 Amendments in This Chapter

[OSHPD 1R, 2 & 5] OSHPD adopts this chapter as amended.

1801.1.3 Identification of Amendments

[OSHPD 1R, 2 & 5] Office of Statewide Hospital Planning and Development (OSHPD) amendments appear in this chapter preceded with the appropriate acronym, as follows:

[OSHPD 1R] — For applications listed in Section 1.10.1.

[OSHPD 2] — For applications listed in Section 1.10.2.

[OSHPD 5] — For applications listed in Section 1.10.5.

Section 1802 Design Basis

1802.1 General

Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2. The quality and design of materials used structurally in excavations and foundations shall comply with the requirements specified in Chapters 16, 19, 21, 22 and 23. Excavations and fills shall comply with Chapter 33.

[HCD 1] For limited-density owner-built rural dwellings, pier foundations, stone masonry footings and foundations, pressure-treated lumber, poles or equivalent foundation materials or designs may be used, provided that the bearing is sufficient for the purpose intended.

Section 1803 Geotechnical Investigations

1803.1 General

Geotechnical investigations shall be conducted in accordance with Section 1803.2 and reported in accordance with Section 1803.6. Where required by the building official or where geotechnical investigations involve in-situ testing, laboratory testing or engineering calculations, such investigations shall be conducted by a registered design professional. [OSHPD 1R, 2 & 5] The classification, testing and investigation of the soil shall be made under the responsible charge of a California registered geotechnical engineer. All recommendations contained in geotechnical and geohazard reports shall be subject to the approval of the enforcement agency. All reports shall be prepared and signed by a registered geotechnical engineer, certified engineering geologist and a registered geophysicist, where applicable.

1803.1.1 General and Where Required for Applications Listed in Section 1.8.2.1.1 Regulated by the Department of Housing and Community Development

[HCD 1] Foundation and soils investigations shall be conducted in conformance with Health and Safety Code Sections 17953 through 17957 as summarized below.

1803.1.1.1 Preliminary Soil Report

Each city, county, or city and county shall enact an ordinance which requires a preliminary soil report, prepared by a civil engineer who is registered by the state. The report shall be based upon adequate test borings or excavations, of every subdivision, where a tentative and final map is required pursuant to Section 66426 of the Government Code.

The preliminary soil report may be waived if the building department of the city, county, or city and county, or other enforcement agency charged with the administration and enforcement of the provisions of Section 1803.1.1, shall determine that, due to the knowledge such department has as to the soil qualities of the soil of the subdivision or lot, no preliminary analysis is necessary.

1803.1.1.2 Soil Investigation by Lot, Necessity, Preparation and Recommendations

If the preliminary soil report indicates the presence of critically expansive soils or other soil problems which, if not corrected, would lead to structural defects, such ordinance shall require a soil investigation of each lot in the subdivision.

The soil investigation shall be prepared by a civil engineer who is registered in this state. It shall recommend corrective action which is likely to prevent structural damage to each dwelling proposed to be constructed on the expansive soil.

1803.1.1.3 Approval, Building Permit Conditions, Appeal

The building department of each city, county, or city and county, or other enforcement agency charged with the administration and enforcement of the provisions of Section 1803.1.1, shall approve the soil investigation if it determines that the recommended action is likely to prevent structural damage to each dwelling to be constructed. As a condition to the building permit, the ordinance shall require that the approved recommended action be incorporated in the construction of each dwelling. Appeal from such determination shall be to the local appeals board.

1803.1.1.4 Liability

A city, county, city and county, or other enforcement agency charged with the administration and enforcement of the provisions of Section 1803.1.1, is not liable for any injury which arises out of any act or omission of the city, county, city and county, other enforcement agency, or a public employee or any other person under Section 1803.1.1.

1803.1.1.5 Alternate Procedures

The governing body of any city, county, or city and county may enact an ordinance prescribing an alternate procedure which is equal to or more restrictive than the procedure specified in Section 1803.1.1.

1803.2 Investigations Required

Geotechnical investigations shall be conducted in accordance with Sections 1803.3 through 1803.5.

Exception: The building official shall be permitted to waive the requirement for a geotechnical investigation where satisfactory data from adjacent areas is available that demonstrates an investigation is not necessary for any of the conditions in Sections 1803.5.1 through 1803.5.6 and Sections 1803.5.10 and 1803.5.11.

[OSHPD 1R, 2 & 5] Geotechnical reports are not required for one-story, wood-frame and light-steel-frame buildings of Type V construction and 4,000 square feet (371 m2) or less in floor area, not located within Earthquake Fault Zones or Seismic Hazard Zones as shown in the most recently published maps from the California Geological Survey (CGS). Allowable foundation and lateral soil pressure values may be determined from Table 1806.2.

1803.3 Basis of Investigation

Soil classification shall be based on observation and any necessary tests of the materials disclosed by borings, test pits or other subsurface exploration made in appropriate locations. Additional studies shall be made as necessary to evaluate slope stability, soil strength, position and adequacy of load-bearing soils, the effect of moisture variation on soil-bearing capacity, compressibility, liquefaction and expansiveness.

1803.3.1 Scope of Investigation

The scope of the geotechnical investigation including the number and types of borings or soundings, the equipment used to drill or sample, the in-situ testing equipment and the laboratory testing program shall be determined by a registered design professional.

[OSHPD 1R, 2 & 5] There shall not be less than one boring or exploration shaft for each 5,000 square feet (465 m2) of building area at the foundation level with a minimum of two provided for any one building. A boring may be considered to reflect subsurface conditions relevant to more than one building, subject to the approval of the enforcement agency.

Borings shall be of sufficient size to permit visual examination of the soil in place or, in lieu thereof, cores shall be taken.

Borings shall be of sufficient depth and size to adequately characterize subsurface conditions.

Exception: Single-story Type V skilled nursing or intermediate care facilities utilizing wood-frame or light-steel frame construction.

1803.4 Qualified Representative

The investigation procedure and apparatus shall be in accordance with generally accepted engineering practice. The registered design professional shall have a fully qualified representative on site during all boring or sampling operations.

1803.5 Investigated Conditions

Geotechnical investigations shall be conducted as indicated in Sections 1803.5.1 through 1803.5.12.

1803.5.1 Classification

Soil materials shall be classified in accordance with ASTM D2487. Rock shall be classified in accordance with ASTM D5878.

1803.5.2 Questionable Soil and Rock

Where the classification, strength, moisture sensitivity or compressibility of the soil or rock is in doubt or where a load-bearing value superior to that specified in this code is claimed, the building official shall be permitted to require that a geotechnical investigation be conducted.

1803.5.3 Expansive Soil

In areas likely to have expansive soil, the building official shall require soil tests to determine where such soils do exist.

Soils meeting all four of the following provisions shall be considered to be expansive, except that tests to show compliance with Items 1, 2 and 3 shall not be required if the test prescribed in Item 4 is conducted:

- Plasticity index (PI) of 15 or greater, determined in accordance with ASTM D4318.

- More than 10 percent of the soil particles pass a No.200 sieve (75 µm), determined in accordance with ASTM D6913.

- More than 10 percent of the soil particles are less than 5 micrometers in size, determined in accordance with ASTM D6913.

- Expansion index greater than 20, determined in accordance with ASTM D4829.

1803.5.4 Groundwater

Diagram

A geotechnical investigation shall be performed to determine if:

- Groundwater is above or within 5 feet (1524 mm) below the elevation of the lowest floor level where such floor is located below the finished ground level adjacent to the foundation.

- The groundwater depth will affect the design and construction of buildings and structures.

UpCodes Diagrams (2)

Primary

Hydrostatic & Hydrodynamic Forces

Dampproofing / Waterproofing: Story Above Grade Plane

1803.5.5 Deep Foundations

Where deep foundations will be used, a geotechnical investigation shall be conducted and shall include all of the following, unless sufficient data on which to base the design and installation is otherwise available:

- Recommended deep foundation types and installed capacities.

- Recommended center-to-center spacing of deep foundation elements.

- Driving criteria.

- Installation procedures.

- Field inspection and reporting procedures (to include procedures for verification of the installed bearing capacity where required).

- Load test requirements.

- Suitability of deep foundation materials for the intended environment.

- Designation of bearing stratum or strata.

- Reductions for group action, where necessary.

1803.5.6 Rock Strata

Where foundations are to be constructed on or in rock, the geotechnical investigation shall assess variations in rock strata depth, competency and load-bearing capacity.

1803.5.7 Excavation Near Foundations

Where excavation will reduce support from any foundation, a registered design professional shall prepare an assessment of the structure as determined from examination of the structure, available design documents, available subsurface data, and, if necessary, excavation of test pits. The registered design professional shall determine the requirements for support and protection of any existing foundation and prepare site-specific plans, details and sequence of work for submission. Such support shall be provided by under-pinning, bracing, excavation retention systems or by other means acceptable to the building official.

1803.5.8 Compacted Fill Material

Where shallow foundations will bear on compacted fill material more than 12 inches (305 mm) in depth, a geotechnical investigation shall be conducted and shall include all of the following:

- Specifications for the preparation of the site prior to placement of compacted fill material.

- Specifications for material to be used as compacted fill.

- Test methods to be used to determine the maximum dry density and optimum moisture content of the material to be used as compacted fill.

- Maximum allowable thickness of each lift of compacted fill material.

- Field test method for determining the in-place dry density of the compacted fill.

- Minimum acceptable in-place dry density expressed as a percentage of the maximum dry density determined in accordance with Item 3.

- Number and frequency of field tests required to determine compliance with Item 6.

1803.5.9 Controlled Low-Strength Material (CLSM)

Where shallow foundations will bear on controlled low-strength material (CLSM), a geotechnical investigation shall be conducted and shall include all of the following:

- Specifications for the preparation of the site prior to placement of the CLSM.

- Specifications for the CLSM.

- Laboratory or field test method(s) to be used to determine the compressive strength or bearing capacity of the CLSM.

- Test methods for determining the acceptance of the CLSM in the field.

- Number and frequency of field tests required to determine compliance with Item 4.

1803.5.10 Alternate Setback and Clearance

Where setbacks or clearances other than those required in Section 1808.7 are desired, the building official shall be permitted to require a geotechnical investigation by a registered design professional to demonstrate that the intent of Section 1808.7 would be satisfied. Such an investigation shall include consideration of material, height of slope, slope gradient, load intensity and erosion characteristics of slope material.

1803.5.11 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F, a geotechnical investigation shall be conducted, and shall include an evaluation of all of the following potential geologic and seismic hazards:

- Slope instability.

- Liquefaction.

- Total and differential settlement.

- Surface displacement due to faulting or seismically induced lateral spreading or lateral flow.

1803.5.12 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, the geotechnical investigation required by Section 1803.5.11 shall include all of the following as applicable:

- The determination of dynamic seismic lateral earth pressures on foundation walls and retaining walls supporting more than 6 feet (1.83 m) of backfill height due to design earthquake ground motions.

- The potential for liquefaction and soil strength loss evaluated for site peak ground acceleration, earthquake magnitude and source characteristics consistent with the maximum considered earthquake ground motions. Peak ground acceleration shall be determined based on one of the following:

  - A site-specific study in accordance with Chapter 21 of ASCE 7.

  - In accordance with Section 11.8.3 of ASCE 7.

- An assessment of potential consequences of liquefaction and soil strength loss including, but not limited to, the following:

  - Estimation of total and differential settlement.

  - Lateral soil movement.

  - Lateral soil loads on foundations.

  - Reduction in foundation soil-bearing capacity and lateral soil reaction.

  - Soil downdrag and reduction in axial and lateral soil reaction for pile foundations.

  - Increases in soil lateral pressures on retaining walls.

  - Flotation of buried structures.

- Discussion of mitigation measures such as, but not limited to, the following:

  - Selection of appropriate foundation type and depths.

  - Selection of appropriate structural systems to accommodate anticipated displacements and forces.

  - Ground stabilization.

  - Any combination of these measures and how they shall be considered in the design of the structure.

1803.6 Reporting

Where geotechnical investigations are required, a written report of the investigations shall be submitted to the building official by the permit applicant at the time of permit application. This geotechnical report shall include, but need not be limited to, the following information:

- A plot showing the location of the soil investigations.

- A complete record of the soil boring and penetration test logs and soil samples.

- A record of the soil profile.

- Elevation of the water table, if encountered.

- Recommendations for foundation type and design criteria, including but not limited to: bearing capacity of natural or compacted soil; provisions to mitigate the effects of expansive soils; mitigation of the effects of liquefaction, differential settlement and varying soil strength; and the effects of adjacent loads.

- Expected total and differential settlement.

- Deep foundation information in accordance with Section 1803.5.5.

- Special design and construction provisions for foundations of structures founded on expansive soils, as necessary.

- Compacted fill material properties and testing in accordance with Section 1803.5.8.

- Controlled low-strength material properties and testing in accordance with Section 1803.5.9.

- [OSHPD 1R, 2 & 5] The report shall consider the effects of seismic hazard in accordance with Section 1803.7.

1803.7 Geohazard Reports

[OSHPD 1R, 2 & 5] Geohazard reports shall be required for all proposed construction.

Exceptions:

- Reports are not required for one-story, wood-frame and light-steel-frame buildings of Type V skilled nursing or intermediate care facilities construction and 4,000 square feet (371 m2) or less in floor area, not located within Earthquake Fault Zones or Seismic Hazard Zones as shown in the most recently published maps from the California Geological Survey (CGS);

- Reports are not required for the following scopes of work in existing buildings:

Nonstructural alterations, voluntary structural alterations without foundation work, and incidental structural additions or alterations, and structural repairs for other than earthquake damage.

- A previous report for a specific site may be resubmitted, provided that a reevaluation is made and the report is found to be currently appropriate.

The purpose of the geohazard report shall be to identify geologic and seismic conditions that may require project mitigations. The reports shall contain data which provide an assessment of the nature of the site and potential for earthquake damage based on appropriate investigations of the regional and site geology, project foundation conditions and the potential seismic shaking at the site. The report shall be prepared by a California-certified engineering geologist in consultation with a California-registered geotechnical engineer.

The preparation of the geohazard report shall consider the most recent CGS Note 48; Checklist for the Review of Engineering Geology and Seismology Reports for California Public School, Hospitals and Essential Services Buildings. In addition, the most recent version of CGS Special Publication 42: Earthquake Fault Zones, A Guide for Government Agencies, Property Owners / Developers, and Geoscience Practitioners for Assessing Fault Rupture Hazards in California, shall be considered for project sites proposed within an Alquist-Priolo Earthquake Fault Zone. The most recent version of CGS Special Publication 117, Guidelines for Evaluating and Mitigating Seismic Hazards in California, shall be considered for project sites proposed within a Seismic Hazard Zone. All conclusions shall be fully supported by satisfactory data and analysis.

In addition to requirements in Sections 1803.5.11 and 1803.5.12, the report shall include, but need not be limited to, the following:

- Site geology.

- Evaluation of the known active and potentially active faults, both regional and local.

- Ground-motion parameters, as required by Section 1613 and ASCE 7.

Section 1804 Excavation, Grading and Fill

Diagram

UpCodes Diagrams (5)

Footings: Setbacks from Descending Slope

Swimming Pools Next to Descending Slopes

Footings: Setback from Steep Slope

Footings: Setback from Ascending Slope

Retaining Wall: Setback at Uphill Slope

1804.1 Excavation Near Foundations

Excavation for any purpose shall not reduce vertical or lateral support for any foundation or adjacent foundation without first underpinning or protecting the foundation against detrimental lateral or vertical movement, or both, in accordance with Section 1803.5.7.

1804.2 Underpinning

Where underpinning is chosen to provide the protection or support of adjacent structures, the underpinning system shall be designed and installed in accordance with provisions of this chapter and Chapter 33.

1804.2.1 Underpinning Sequencing

Underpinning shall be installed in a sequential manner that protects the neighboring structure and the working construction site. The sequence of installation shall be identified in the approved construction documents.

1804.3 Placement of Backfill

The excavation outside the foundation shall be backfilled with soil that is free of organic material, construction debris, cobbles and boulders or with a controlled low-strength material (CLSM). The backfill shall be placed in lifts and compacted in a manner that does not damage the foundation or the waterproofing or dampproofing material.

Exception: CLSM need not be compacted.

1804.4 Site Grading

Diagram

The ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than 1 unit vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. If physical obstructions or lot lines prohibit 10 feet (3048 mm) of horizontal distance, a 5-percent slope shall be provided to an approved alternative method of diverting water away from the foundation. Swales used for this purpose shall be sloped not less than 2 percent where located within 10 feet (3048 mm) of the building foundation. Impervious surfaces within 10 feet (3048 mm) of the building foundation shall be sloped not less than 2 percent away from the building.

Exceptions:

- Where climatic or soil conditions warrant, the slope of the ground away from the building foundation shall be permitted to be reduced to not less than 1 unit vertical in 48 units horizontal (2-percent slope).

- Impervious surfaces shall be permitted to be sloped less than 2 percent where the surface is a door landing or ramp that is required to comply with Section 1010.1.4, 1012.3 or 1012.6.1.

The procedure used to establish the final ground level adjacent to the foundation shall account for additional settlement of the backfill.

UpCodes Diagram (1)

Surface Drainage of Stormwater

1804.4.1 [HCD 1] Construction Plans

Construction plans shall indicate how the site grading or drainage system will manage all surface water flows to keep water from entering buildings in accordance with the California Green Building Standards Code (CALGreen), Chapter 4, Division 4.1.

1804.5 Grading and Fill in Flood Hazard Areas

In flood hazard areas established in Section 1612.3, grading, fill, or both, shall not be approved:

- Unless such fill is placed, compacted and sloped to minimize shifting, slumping and erosion during the rise and fall of flood water and, as applicable, wave action.

- In floodways, unless it has been demonstrated through hydrologic and hydraulic analyses performed by a registered design professional in accordance with standard engineering practice that the proposed grading or fill, or both, will not result in any increase in flood levels during the occurrence of the design flood.

- In coastal high hazard areas, unless such fill is conducted or placed to avoid diversion of water and waves toward any building or structure.

- Where design flood elevations are specified but floodways have not been designated, unless it has been demonstrated that the cumulative effect of the proposed flood hazard area encroachment, when combined with all other existing and anticipated flood hazard area encroachment, will not increase the design flood elevation more than 1 foot (305 mm) at any point.

1804.6 Compacted Fill Material

Where shallow foundations will bear on compacted fill material, the compacted fill shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803.

Exception: Compacted fill material 12 inches (305 mm) in depth or less need not comply with an approved report, provided that the in-place dry density is not less than 90 percent of the maximum dry density at optimum moisture content determined in accordance with ASTM D1557. The compaction shall be verified by special inspection in accordance with Section 1705.6.

1804.7 Controlled Low-Strength Material (CLSM)

Where shallow foundations will bear on controlled low-strength material (CLSM), the CLSM shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803.

Section 1805 Dampproofing and Waterproofing

Diagram

UpCodes Diagrams (4)

Subgrade Floor Waterproofing

Subgrade Wall Waterproofing

Dampproofing / Waterproofing: Story Above Grade Plane

Damproofing of Floors

1805.1 General

Diagram

Walls or portions thereof that retain earth and enclose interior spaces and floors below grade shall be waterproofed and dampproofed in accordance with this section, with the exception of those spaces containing groups other than residential and institutional where such omission is not detrimental to the building or occupancy.

Ventilation for crawl spaces shall comply with Section 1202.4.

UpCodes Diagram (1)

Primary

Cement Coat Waterproofing Example

1805.1.1 Story Above Grade Plane

Diagram

Where a basement is considered a story above grade plane and the finished ground level adjacent to the basement wall is below the basement floor elevation for 25 percent or more of the perimeter, the floor and walls shall be dampproofed in accordance with Section 1805.2 and a foundation drain shall be installed in accordance with Section 1805.4.2. The foundation drain shall be installed around the portion of the perimeter where the basement floor is below ground level. The provisions of Sections 1803.5.4, 1805.3 and 1805.4.1 shall not apply in this case.

UpCodes Diagrams (3)

Primary

Dampproofing / Waterproofing: Story Above Grade Plane

Story Above Grade Plane

Grade Plane

1805.1.2 Under-Floor Space

Diagram

The finished ground level of an under-floor space such as a crawl space shall not be located below the bottom of the footings. Where there is evidence that the ground-water table rises to within 6 inches (152 mm) of the ground level at the outside building perimeter, or that the surface water does not readily drain from the building site, the ground level of the under-floor space shall be as high as the outside finished ground level, unless an approved drainage system is provided. The provisions of Sections 1803.5.4, 1805.2, 1805.3 and 1805.4 shall not apply in this case.

UpCodes Diagram (1)

Primary

Finish Grade at Under-floor Surfaces

1805.1.2.1 Flood Hazard Areas

Diagram

For buildings and structures in flood hazard areas as established in Section 1612.3, the finished ground level of an under-floor space such as a crawl space shall be equal to or higher than the outside finished ground level on one side or more.

Exception: Under-floor spaces of Group R-3 buildings that meet the requirements of FEMA TB 11.

UpCodes Diagrams (4)

Enclosures with Flood Openings: Zone A

Below Grade Crawlspaces in Zone A (FEMA)

Flood: Wet Floodproofing Garages, Crawlspaces

Flood Venting Layout

1805.1.3 Ground-Water Control

Where the ground-water table is lowered and maintained at an elevation not less than 6 inches (152 mm) below the bottom of the lowest floor, the floor and walls shall be dampproofed in accordance with Section 1805.2. The design of the system to lower the ground-water table shall be based on accepted principles of engineering that shall consider, but not necessarily be limited to, permeability of the soil, rate at which water enters the drainage system, rated capacity of pumps, head against which pumps are to operate and the rated capacity of the disposal area of the system.

1805.2 Dampproofing

Where hydrostatic pressure will not occur as determined by Section 1803.5.4, floors and walls for other than wood foundation systems shall be dampproofed in accordance with this section. [OSHPD 1R, 2 & 5] Wood foundation systems are not permitted by OSHPD. Wood foundation systems shall be constructed in accordance with AWC PWF.

1805.2.1 Floors

Diagram

Dampproofing materials for floors shall be installed between the floor and the base course required by Section 1805.4.1, except where a separate floor is provided above a concrete slab.

Where installed beneath the slab, dampproofing shall consist of not less than 6-mil (0.006 inch; 0.152 mm) polyethylene with joints lapped not less than 6 inches (152 mm), or other approved methods or materials. Where permitted to be installed on top of the slab, dampproofing shall consist of mopped-on bitumen, not less than 4-mil (0.004 inch; 0.102 mm) polyethylene, or other approved methods or materials. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

UpCodes Diagram (1)

Primary

Damproofing of Floors

1805.2.2 Walls

Diagram

Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level.

Dampproofing shall consist of a bituminous material, 3 pounds per square yard (16 N/m2) of acrylic modified cement, 1/8 inch (3.2 mm) coat of surface-bonding mortar complying with ASTM C887, any of the materials permitted for waterproofing by Section 1805.3.2 or other approved methods or materials.

UpCodes Diagram (1)

Subgrade Wall Waterproofing

1805.2.2.1 Surface Preparation of Walls

Prior to application of dampproofing materials on concrete walls, holes and recesses resulting from the removal of form ties shall be sealed with a bituminous material or other approved methods or materials. Unit masonry walls shall be parged on the exterior surface below ground level with not less than 3/8 inch (9.5 mm) of Portland cement mortar. The parging shall be coved at the footing.

Exception: Parging of unit masonry walls is not required where a material is approved for direct application to the masonry.

1805.3 Waterproofing

Diagram

Where the ground-water investigation required by Section 1803.5.4 indicates that a hydrostatic pressure condition exists, and the design does not include a ground-water control system as described in Section 1805.1.3, walls and floors shall be waterproofed in accordance with this section.

UpCodes Diagram (1)

Hydrostatic & Hydrodynamic Forces

1805.3.1 Floors

Diagram

Floors required to be waterproofed shall be of concrete and designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected.

Waterproofing shall be accomplished by placing a membrane of rubberized asphalt, butyl rubber, fully adhered/fully bonded HDPE or polyolefin composite membrane or not less than 6-mil [0.006 inch (0.152 mm)] polyvinyl chloride with joints lapped not less than 6 inches (152 mm) or other approved materials under the slab. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

UpCodes Diagram (1)

Primary

Subgrade Floor Waterproofing

1805.3.2 Walls

Diagram

Walls required to be waterproofed shall be of concrete or masonry and shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected.

Waterproofing shall be applied from the bottom of the wall to not less than 12 inches (305 mm) above the maximum elevation of the ground-water table. The remainder of the wall shall be dampproofed in accordance with Section 1805.2.2. Waterproofing shall consist of two-ply hot-mopped felts, not less than 6-mil (0.006 inch; 0.152 mm) polyvinyl chloride, 40-mil (0.040 inch; 1.02 mm) polymer-modified asphalt, 6-mil (0.006 inch; 0.152 mm) polyethylene or other approved methods or materials capable of bridging nonstructural cracks. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

UpCodes Diagram (1)

Primary

Subgrade Wall Waterproofing

1805.3.2.1 Surface Preparation of Walls

Prior to the application of waterproofing materials on concrete or masonry walls, the walls shall be prepared in accordance with Section 1805.2.2.1.

1805.3.3 Joints and Penetrations

Joints in walls and floors, joints between the wall and floor and penetrations of the wall and floor shall be made watertight utilizing approved methods and materials.

1805.4 Subsoil Drainage System

Diagram

Where a hydrostatic pressure condition does not exist, dampproofing shall be provided and a base shall be installed under the floor and a drain installed around the foundation perimeter. A subsoil drainage system designed and constructed in accordance with Section 1805.1.3 shall be deemed adequate for lowering the ground-water table.

UpCodes Diagram (1)

Primary

Subsoil Sump Pump and Discharge

1805.4.1 Floor Base Course

Floors of basements, except as provided for in Section 1805.1.1, shall be placed over a floor base course not less than 4 inches (102 mm) in thickness that consists of gravel or crushed stone containing not more than 10 percent of material that passes through a No. 4 (4.75 mm) sieve.

Exceptions:

- Where a site is located in well-drained gravel or sand/gravel mixture soils, a floor base course is not required.

- [HCD 1] When a capillary break is installed in accordance with the California Green Building Standards Code (CALGreen), Chapter 4, Division 4.5.

1805.4.2 Foundation Drain

Diagram

A drain shall be placed around the perimeter of a foundation that consists of gravel or crushed stone containing not more than 10-percent material that passes through a No. 4 (4.75 mm) sieve. The drain shall extend not less than 12 inches (305 mm) beyond the outside edge of the footing. The thickness shall be such that the bottom of the drain is not higher than the bottom of the base under the floor, and that the top of the drain is not less than 6 inches (152 mm) above the top of the footing. The top of the drain shall be covered with an approved filter membrane material. Where a drain tile or perforated pipe is used, the invert of the pipe or tile shall not be higher than the floor elevation. The top of joints or the top of perforations shall be protected with an approved filter membrane material. The pipe or tile shall be placed on not less than 2 inches (51 mm) of gravel or crushed stone complying with Section 1805.4.1, and shall be covered with not less than 6 inches (152 mm) of the same material.

UpCodes Diagrams (2)

Primary

Prescriptive Foundation Wall and Drain

Dampproofing / Waterproofing: Story Above Grade Plane

1805.4.3 Drainage Discharge

Diagram

The floor base and foundation perimeter drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the California Plumbing Code.

Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a dedicated drainage system is not required.

UpCodes Diagram (1)

Subsoil Sump Pump and Discharge

Section 1806 Presumptive Load-Bearing Values of Soils

1806.1 Load Combinations

The presumptive load-bearing values provided in Table 1806.2 shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2. The values of vertical foundation pressure and lateral bearing pressure given in Table 1806.2 shall be permitted to be increased by one-third where used with the alternative allowable stress design load combinations of Section 1605.2 that include wind or earthquake loads.

1806.2 Presumptive Load-Bearing Values

Diagram

The load-bearing values used in design for supporting soils and rock near the surface shall not exceed the values specified in Table 1806.2 unless data to substantiate the use of higher values are submitted and approved. Where the building official has reason to doubt the classification, strength or compressibility of the soil or rock, the requirements of Section 1803.5.2 shall be satisfied.

Presumptive load-bearing values shall apply to materials with similar physical and engineering characteristics. Mud, organic silt and organic clays (OL, OH), peat (Pt) and undocumented fill shall not be assumed to have a presumptive load-bearing capacity unless data to substantiate the use of such a value are submitted.

Exception: A presumptive load-bearing capacity shall be permitted to be used where the building official deems the load-bearing capacity is adequate for the support of lightweight or temporary structures.

TABLE 1806.2—PRESUMPTIVE LOAD-BEARING VALUES

| CLASS OF MATERIALS | VERTICAL FOUNDATION PRESSURE (psf) | LATERAL BEARING PRESSURE (psf/ft below natural grade) | LATERAL SLIDING RESISTANCE |  |
| --- | --- | --- | --- | --- |
|  |  |  | Coefficient of frictiona | Cohesion (psf)b |
| 1. Crystalline bedrock | 12,000 | 1,200 | 0.70 | — |
| 2. Sedimentary and foliated rock | 4,000 | 400 | 0.35 | — |
| 3. Sandy gravel and gravel (GW and GP) | 3,000 | 200 | 0.35 | — |
| 4. Sand, silty sand, clayey sand, silty gravel and clayey gravel (SW, SP, SM, SC, GM and GC) | 2,000 | 150 | 0.25 | — |
| 5. Clay, sandy clay, silty clay, clayey silt, silt and sandy silt (CL, ML, MH and CH) | 1,500 | 100 | — | 130 |

For SI: 1 pound per square foot = 0.0479 kPa, 1 pound per square foot per foot = 0.157 kPa/m.

- Coefficient to be multiplied by the dead load.

- Cohesion value to be multiplied by the contact area, as limited by Section 1806.3.2.

UpCodes Diagram (1)

Interior Column on Footing w/o Pier

1806.3 Lateral Load Resistance

Where the presumptive values of Table 1806.2 are used to determine resistance to lateral loads, the calculations shall be in accordance with Sections 1806.3.1 through 1806.3.4.

1806.3.1 Combined Resistance

The total resistance to lateral loads shall be permitted to be determined by combining the values derived from the lateral bearing pressure and the lateral sliding resistance specified in Table 1806.2.

1806.3.2 Lateral Sliding Resistance Limit

For clay, sandy clay, silty clay, clayey silt, silt and sandy silt, the lateral sliding resistance shall not exceed one-half the dead load.

1806.3.3 Increase for Depth

The lateral bearing pressures specified in Table 1806.2 shall be permitted to be increased by the tabular value for each additional foot (305 mm) of depth to a value that is not greater than 15 times the tabular value.

1806.3.4 Increase for Poles

Isolated poles for uses such as flagpoles or signs and poles used to support buildings that are not adversely affected by a 1/2-inch (12.7 mm) motion at the ground surface due to short-term lateral loads shall be permitted to be designed using lateral bearing pressures equal to two times the tabular values.

Section 1807 Foundation Walls, Retaining Walls and Embedded Posts and Poles

Diagram

UpCodes Diagrams (7)

Wall Sleeve: Example

Footings: Setbacks from Descending Slope

Swimming Pools Next to Descending Slopes

Footings: Setback from Steep Slope

Footings: Setback from Ascending Slope

Retaining Wall: Setback at Uphill Slope

Guards at Retaining Walls

1807.1 Foundation Walls

Diagram

Foundation walls shall be designed and constructed in accordance with Sections 1807.1.1 through 1807.1.6. Foundation walls shall be supported by foundations designed in accordance with Section 1808.

UpCodes Diagrams (2)

Piping Through Foundation Wall (UPC)

Continuous Insulation

Building products (4)

FOAMULAR® NGX® 150

Owens Corning

FOAMULAR® NGX® 250

Owens Corning

FOAMULAR® NGX® 400/600/1000

Owens Corning

FOAMULAR® Project Wall Panels

Owens Corning

1807.1.1 Design Lateral Soil Loads

Foundation walls shall be designed for the lateral soil loads set forth in Section 1610.

1807.1.2 Unbalanced Backfill Height

Unbalanced backfill height is the difference in height between the exterior finish ground level and the lower of the top of the concrete footing that supports the foundation wall or the interior finish ground level. Where an interior concrete slab on grade is provided and is in contact with the interior surface of the foundation wall, the unbalanced backfill height shall be permitted to be measured from the exterior finish ground level to the top of the interior concrete slab.

1807.1.3 Rubble Stone Foundation Walls

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Foundation walls of rough or random rubble stone shall be not less than 16 inches (406 mm) thick. Rubble stone shall not be used for foundation walls of structures assigned to Seismic Design Category C, D, E or F.

1807.1.4 Permanent Wood Foundation Systems

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Permanent wood foundation systems shall be designed and installed in accordance with AWC PWF. Lumber and plywood shall be preservative treated in accordance with AWPA U1 (Commodity Specification A, Special Requirement 4.2) and shall be identified in accordance with Section 2303.1.9.1.

1807.1.5 Concrete and Masonry Foundation Walls

Concrete and masonry foundation walls shall be designed in accordance with Chapter 19 or 21, as applicable.

Exception: [OSHPD 1R, 2 & 5] Not permitted by OSHPD. Concrete and masonry foundation walls shall be permitted to be designed and constructed in accordance with Section 1807.1.6.

1807.1.6 Prescriptive Design of Concrete and Masonry Foundation Walls

Diagram

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Concrete and masonry foundation walls that are laterally supported at the top and bottom shall be permitted to be designed and constructed in accordance with this section.

UpCodes Diagrams (2)

Prescriptive Foundation Wall and Drain

Decay Resistance at Below Grade Walls

1807.1.6.1 Foundation Wall Thickness

The thickness of prescriptively designed foundation walls shall be not less than the thickness of the wall supported, except that foundation walls of not less than 8-inch (203 mm) nominal width shall be permitted to support brick-veneered frame walls and 10-inch-wide (254 mm) cavity walls provided that the requirements of Section 1807.1.6.2 or 1807.1.6.3 are met.

Building products (24)

8 Square 4 x 8 x 8

Interstate Brick

Atlas® 10 x 2¼ x 16

Interstate Brick

Atlas® 10 x 4 x 16

Interstate Brick

Atlas® 6 x 2¼ x 12

Interstate Brick

Atlas® 6 x 2¼ x 16

Interstate Brick

Atlas® 6 x 4 x 16

Interstate Brick

Atlas® 8 x 2¼ x 16

Interstate Brick

Atlas® 8 x 4 x 12

Interstate Brick

Atlas® 8 x 4 x 16

Interstate Brick

Atlas® Emperor 4 x 4 x 16

Interstate Brick

Atlas® Utility 4 x 4 x 12

Interstate Brick

Closure 4 x 4 x 8

Interstate Brick

Emperor 4 x 2¼ x 16

Interstate Brick

Emperor 4 x 4 x 16

Interstate Brick

Engineer 4 x 2¾ x 8

Interstate Brick

FOAMGLAS® Perinsul® SIB

Owens Corning

King 3 x 3 x 10

Interstate Brick

Modular 4 x 2¼ x 8

Interstate Brick

Norman 4 x 2¼ x 12

Interstate Brick

Roman

Interstate Brick

Roman Emperor

Interstate Brick

Super Atlas® 8 x 8 x16

Interstate Brick

Super Emperor 4 x 8 x 16

Interstate Brick

Utility 4 x 4 x 12

Interstate Brick

1807.1.6.2 Concrete Foundation Walls

Concrete foundation walls shall comply with the following:

- The thickness shall comply with the requirements of Table 1807.1.6.2.

- The size and spacing of vertical reinforcement shown in Table 1807.1.6.2 are based on the use of reinforcement with a minimum yield strength of 60,000 pounds per square inch (psi) (414 MPa). Vertical reinforcement with a minimum yield strength of 40,000 psi (276 MPa) or 50,000 psi (345 MPa) shall be permitted, provided that the same size bar is used and the spacing shown in the table is reduced by multiplying the spacing by 0.67 or 0.83, respectively.

- Vertical reinforcement, where required, shall be placed nearest the inside face of the wall a distance, d, from the outside face (soil face) of the wall. The distance, d, is equal to the wall thickness, t, minus 1.25 inches (32 mm) plus one-half the bar diameter, db, [d = t — (1.25 + db/2)]. The reinforcement shall be placed within a tolerance of ± 3/8 inch (9.5 mm) where d is less than or equal to 8 inches (203 mm) or ± 1/2 inch (12.7 mm) where d is greater than 8 inches (203 mm).

- In lieu of the reinforcement shown in Table 1807.1.6.2, smaller reinforcing bar sizes with closer spacings that provide an equivalent cross-sectional area of reinforcement per unit length shall be permitted.

- Concrete cover for reinforcement measured from the inside face of the wall shall be not less than 3/4 inch (19.1 mm). Concrete cover for reinforcement measured from the outside face of the wall shall be not less than 11/2 inches (38 mm) for No. 5 bars and smaller, and not less than 2 inches (51 mm) for larger bars.

- Concrete shall have a specified compressive strength, f'c, of not less than 2,500 psi (17.2 MPa).

- The unfactored axial load per linear foot of wall shall not exceed 1.2 tf'c where t is the specified wall thickness in inches.

TABLE 1807.1.6.2—CONCRETE FOUNDATION WALLSb, c

| MAXIMUM WALL HEIGHT (feet) | MAXIMUM UNBALANCED BACKFILL HEIGHTe (feet) | MINIMUM VERTICAL REINFORCEMENT-BAR SIZE AND SPACING (inches) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Design lateral soil loada (psf per foot of depth) |  |  |  |  |  |  |  |  |
|  |  | 30d |  |  | 45d |  |  | 60 |  |  |
|  |  | Minimum wall thickness (inches) |  |  |  |  |  |  |  |  |
|  |  | 7.5 | 9.5 | 11.5 | 7.5 | 9.5 | 11.5 | 7.5 | 9.5 | 11.5 |
| 5 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
| 6 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 6 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
| 7 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 6 | PC | PC | PC | PC | PC | PC | #5 at 48 | PC | PC |
|  | 7 | PC | PC | PC | #5 at 46 | PC | PC | #6 at 48 | PC | PC |
| 8 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 6 | PC | PC | PC | PC | PC | PC | #5 at 43 | PC | PC |
|  | 7 | PC | PC | PC | #5 at 41 | PC | PC | #6 at 43 | PC | PC |
|  | 8 | #5 at 47 | PC | PC | #6 at 43 | PC | PC | #6 at 32 | #6 at 44 | PC |
| 9 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 6 | PC | PC | PC | PC | PC | PC | #5 at 39 | PC | PC |
|  | 7 | PC | PC | PC | #5 at 37 | PC | PC | #6 at 38 | #5 at 37 | PC |
|  | 8 | #5 at 41 | PC | PC | #6 at 38 | #5 at 37 | PC | #7 at 39 | #6 at 39 | #4 at 48 |
|  | 9d | #6 at 46 | PC | PC | #7 at 41 | #6 at 41 | PC | #7 at 31 | #7 at 41 | #6 at 39 |
| 10 | 4 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 5 | PC | PC | PC | PC | PC | PC | PC | PC | PC |
|  | 6 | PC | PC | PC | PC | PC | PC | #5 at 37 | PC | PC |
|  | 7 | PC | PC | PC | #6 at 48 | PC | PC | #6 at 35 | #6 at 48 | PC |
|  | 8 | #5 at 38 | PC | PC | #7 at 47 | #6 at 47 | PC | #7 at 35 | #7 at 47 | #6 at 45 |
|  | 9d | #6 at 41 | #4 at 48 | PC | #7 at 37 | #7 at 48 | #4 at 48 | #6 at 22 | #7 at 37 | #7 at 47 |
|  | 10d | #7 at 45 | #6 at 45 | PC | #7 at 31 | #7 at 40 | #6 at 38 | #6 at 22 | #7 at 30 | #7 at 38 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot per foot = 0.157 kPa/m.

- For design lateral soil loads, see Section 1610.

- Provisions for this table are based on design and construction requirements specified in Section 1807.1.6.2.

- PC = Plain Concrete.

- Where unbalanced backfill height exceeds 8 feet and design lateral soil loads from Table 1610.1 are used, the requirements for 30 and 45 psf per foot of depth are not applicable (see Section 1610).

- For height of unbalanced backfill, see Section 1807.1.2.

1807.1.6.2.1 Seismic Requirements

Based on the seismic design category assigned to the structure in accordance with Section 1613, concrete foundation walls designed using Table 1807.1.6.2 shall be subject to the following limitations:

- Seismic Design Categories A and B. Not less than one No. 5 bar shall be provided around window, door and similar sized openings. The bar shall be anchored to develop fy in tension at the corners of openings.

- Seismic Design Categories C, D, E and F. Tables shall not be used except as allowed for plain concrete members in Section 1905.6.2.

1807.1.6.3 Masonry Foundation Walls

Masonry foundation walls shall comply with the following:

- The thickness shall comply with the requirements of Table 1807.1.6.3(1) for plain masonry walls or Table 1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4) for masonry walls with reinforcement.

- Vertical reinforcement shall have a minimum yield strength of 60,000 psi (414 MPa).

- The specified location of the reinforcement shall equal or exceed the effective depth distance, d, noted in Tables 1807.1.6.3(2), 1807.1.6.3(3) and 1807.1.6.3(4) and shall be measured from the face of the exterior (soil) side of the wall to the center of the vertical reinforcement. The reinforcement shall be placed within the tolerances specified in TMS 602 for the specified location.

- Grout shall comply with Section 2103.3.

- Concrete masonry units shall comply with ASTM C90.

- Clay masonry units shall comply with ASTM C652 for hollow brick, except compliance with ASTM C62 or ASTM C216 shall be permitted where solid masonry units are installed in accordance with Table 1807.1.6.3(1) for plain masonry.

- Masonry units shall be laid in running bond and installed with Type M or S mortar in accordance with Section 2103.2.1.

- The unfactored axial load per linear foot of wall shall not exceed 1.2 tf'm where t is the specified wall thickness in inches and f'm is the specified compressive strength of masonry in pounds per square inch.

- Not less than 4 inches (102 mm) of solid masonry shall be provided at girder supports at the top of hollow masonry unit foundation walls.

- Corbeling of masonry shall be in accordance with Section 2104.1. Where an 8-inch (203 mm) wall is corbeled, the top corbel shall not extend higher than the bottom of the floor framing and shall be a full course of headers not less than 6 inches (152 mm) in length or the top course bed joint shall be tied to the vertical wall projection. The tie shall be W2.8 (4.8 mm) and spaced at a maximum horizontal distance of 36 inches (914 mm). The hollow space behind the corbelled masonry shall be filled with mortar or grout.

TABLE 1807.1.6.3(1)—PLAIN MASONRY FOUNDATION WALLSa, b, c

| MAXIMUM WALL HEIGHT (feet) | MAXIMUM UNBALANCED BACKFILL HEIGHTe (feet) | MINIMUM NOMINAL WALL THICKNESS (inches) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Design lateral soil loada (psf per foot of depth) |  |  |
|  |  | 30f | 45f | 60 |
| 7 | 4 (or less) | 8 | 8 | 8 |
|  | 5 | 8 | 10 | 10 |
|  | 6 | 10 | 12 | 10 (solidc) |
|  | 7 | 12 | 10 (solidc) | 10 (solidc) |
| 8 | 4 (or less) | 8 | 8 | 8 |
|  | 5 | 8 | 10 | 12 |
|  | 6 | 10 | 12 | 12 (solidc) |
|  | 7 | 12 | 12 (solidc) | Note d |
|  | 8 | 10 (solidc) | 12 (solidc) | Note d |
| 9 | 4 (or less) | 8 | 8 | 8 |
|  | 5 | 8 | 10 | 12 |
|  | 6 | 12 | 12 | 12 (solidc) |
|  | 7 | 12 (solidc) | 12 (solidc) | Note d |
|  | 8 | 12 (solidc) | Note d | Note d |
|  | 9f | Note d | Note d | Note d |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot per foot = 0.157 kPa/m.

- For design lateral soil loads, see Section 1610.

- Provisions for this table are based on design and construction requirements specified in Section 1807.1.6.3.

- Solid grouted hollow units or solid masonry units.

- A design in compliance with Chapter 21 or reinforcement in accordance with Table 1807.1.6.3(2) is required.

- For height of unbalanced backfill, see Section 1807.1.2.

- Where unbalanced backfill height exceeds 8 feet and design lateral soil loads from Table 1610.1 are used, the requirements for 30 and 45 psf per foot of depth are not applicable (see Section 1610).

TABLE 1807.1.6.3(2)—8-INCH MASONRY FOUNDATION WALLS WITH REINFORCEMENT WHERE d ≥ 5 INCHESa, b, c

| MAXIMUM WALL HEIGHT (feet-inches) | MAXIMUM UNBALANCED BACKFILL HEIGHTd (feet-inches) | MINIMUM VERTICAL REINFORCEMENT-BAR SIZE AND SPACING (inches) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Design lateral soil loada (psf per foot of depth) |  |  |
|  |  | 30e | 45e | 60 |
| 7-4 | 4-0 (or less) | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 5-0 | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 6-0 | #4 at 48 | #5 at 48 | #5 at 48 |
|  | 7-4 | #5 at 48 | #6 at 48 | #7 at 48 |
| 8-0 | 4-0 (or less) | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 5-0 | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 6-0 | #4 at 48 | #5 at 48 | #5 at 48 |
|  | 7-0 | #5 at 48 | #6 at 48 | #7 at 48 |
|  | 8-0 | #5 at 48 | #6 at 48 | #7 at 48 |
| 8-8 | 4-0 (or less) | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 5-0 | #4 at 48 | #4 at 48 | #5 at 48 |
|  | 6-0 | #4 at 48 | #5 at 48 | #6 at 48 |
|  | 7-0 | #5 at 48 | #6 at 48 | #7 at 48 |
|  | 8-8e | #6 at 48 | #7 at 48 | #8 at 48 |
| 9-4 | 4-0 (or less) | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 5-0 | #4 at 48 | #4 at 48 | #5 at 48 |
|  | 6-0 | #4 at 48 | #5 at 48 | #6 at 48 |
|  | 7-0 | #5 at 48 | #6 at 48 | #7 at 48 |
|  | 8-0 | #6 at 48 | #7 at 48 | #8 at 48 |
|  | 9-4e | #7 at 48 | #8 at 48 | #9 at 48 |
| 10-0 | 4-0 (or less) | #4 at 48 | #4 at 48 | #4 at 48 |
|  | 5-0 | #4 at 48 | #4 at 48 | #5 at 48 |
|  | 6-0 | #4 at 48 | #5 at 48 | #6 at 48 |
|  | 7-0 | #5 at 48 | #6 at 48 | #7 at 48 |
|  | 8-0 | #6 at 48 | #7 at 48 | #8 at 48 |
|  | 9-0e | #7 at 48 | #8 at 48 | #9 at 48 |
|  | 10-10e | #7 at 48 | #9 at 48 | #9 at 48 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot per foot = 0.157 kPa/m.

- For design lateral soil loads, see Section 1610.

- Provisions for this table are based on design and construction requirements specified in Section 1807.1.6.3.

- For alternative reinforcement, see Section 1807.1.6.3.1.

- For height of unbalanced backfill, see Section 1807.1.2.

- Where unbalanced backfill height exceeds 8 feet and design lateral soil loads from Table 1610.1 are used, the requirements for 30 and 45 psf per foot of depth are not applicable. See Section 1610.

TABLE 1807.1.6.3(3)—10-INCH MASONRY FOUNDATION WALLS WITH REINFORCEMENT WHERE d ≥ 6.75 INCHESa, b, c

| MAXIMUM WALL HEIGHT (feet-inches) | MAXIMUM UNBALANCED BACKFILL HEIGHTd (feet-inches) | MINIMUM VERTICAL REINFORCEMENT-BAR SIZE AND SPACING (inches) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Design lateral soil loada (psf per foot of depth) |  |  |
|  |  | 30e | 45e | 60 |
| 7-4 | 4-0 (or less) | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 5-0 | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 6-0 | #4 at 56 | #4 at 56 | #5 at 56 |
|  | 7-4 | #4 at 56 | #5 at 56 | #6 at 56 |
| 8-0 | 4-0 (or less) | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 5-0 | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 6-0 | #4 at 56 | #4 at 56 | #5 at 56 |
|  | 7-0 | #4 at 56 | #5 at 56 | #6 at 56 |
|  | 8-0 | #5 at 56 | #6 at 56 | #7 at 56 |
| 8-8 | 4-0 (or less) | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 5-0 | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 6-0 | #4 at 56 | #4 at 56 | #5 at 56 |
|  | 7-0 | #4 at 56 | #5 at 56 | #6 at 56 |
|  | 8-8e | #5 at 56 | #7 at 56 | #8 at 56 |
| 9-4 | 4-0 (or less) | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 5-0 | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 6-0 | #4 at 56 | #5 at 56 | #5 at 56 |
|  | 7-0 | #4 at 56 | #5 at 56 | #6 at 56 |
|  | 8-0 | #5 at 56 | #6 at 56 | #7 at 56 |
|  | 9-4e | #6 at 56 | #7 at 56 | #7 at 56 |
| 10-0 | 4-0 (or less) | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 5-0 | #4 at 56 | #4 at 56 | #4 at 56 |
|  | 6-0 | #4 at 56 | #5 at 56 | #5 at 56 |
|  | 7-0 | #5 at 56 | #6 at 56 | #7 at 56 |
|  | 8-0 | #5 at 56 | #7 at 56 | #8 at 56 |
|  | 9-0e | #6 at 56 | #7 at 56 | #9 at 56 |
|  | 10-0e | #7 at 56 | #8 at 56 | #9 at 56 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot per foot = 1.157 kPa/m.

- For design lateral soil loads, see Section 1610.

- Provisions for this table are based on design and construction requirements specified in Section 1807.1.6.3.

- For alternative reinforcement, see Section 1807.1.6.3.1.

- For height of unbalanced backfill, see Section 1807.1.2.

- Where unbalanced backfill height exceeds 8 feet and design lateral soil loads from Table 1610.1 are used, the requirements for 30 and 45 psf per foot of depth are not applicable. See Section 1610.

TABLE 1807.1.6.3(4)—12-INCH MASONRY FOUNDATION WALLS WITH REINFORCEMENT WHERE d ≥ 8.75 INCHESa, b, c

| MAXIMUM WALL HEIGHT (feet-inches) | MAXIMUM UNBALANCED BACKFILL HEIGHTd (feet-inches) | MINIMUM VERTICAL REINFORCEMENT-BAR SIZE AND SPACING (inches) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Design lateral soil loada (psf per foot of depth) |  |  |
|  |  | 30e | 45e | 60 |
| 7-4 | 4 (or less) | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 5-0 | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 6-0 | #4 at 72 | #4 at 72 | #5 at 72 |
|  | 7-4 | #4 at 72 | #5 at 72 | #6 at 72 |
| 8-0 | 4 (or less) | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 5-0 | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 6-0 | #4 at 72 | #4 at 72 | #5 at 72 |
|  | 7-0 | #4 at 72 | #5 at 72 | #6 at 72 |
|  | 8-0 | #5 at 72 | #6 at 72 | #8 at 72 |
| 8-8 | 4 (or less) | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 5-0 | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 6-0 | #4 at 72 | #4 at 72 | #5 at 72 |
|  | 7-0 | #4 at 72 | #5 at 72 | #6 at 72 |
|  | 8-8e | #5 at 72 | #7 at 72 | #8 at 72 |
| 9-4 | 4 (or less) | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 5-0 | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 6-0 | #4 at 72 | #5 at 72 | #5 at 72 |
|  | 7-0 | #4 at 72 | #5 at 72 | #6 at 72 |
|  | 8-0 | #5 at 72 | #6 at 72 | #7 at 72 |
|  | 9-4e | #6 at 72 | #7 at 72 | #8 at 72 |
| 10-0 | 4 (or less) | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 5-0 | #4 at 72 | #4 at 72 | #4 at 72 |
|  | 6-0 | #4 at 72 | #5 at 72 | #5 at 72 |
|  | 7-0 | #4 at 72 | #6 at 72 | #6 at 72 |
|  | 8-0 | #5 at 72 | #6 at 72 | #7 at 72 |
|  | 9-0e | #6 at 72 | #7 at 72 | #8 at 72 |
|  | 10-0e | #7 at 72 | #8 at 72 | #9 at 72 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot per foot = 0.157 kPa/m.

- For design lateral soil loads, see Section 1610.

- Provisions for this table are based on design and construction requirements specified in Section 1807.1.6.3.

- For alternative reinforcement, see Section 1807.1.6.3.1.

- For height of unbalanced backfill, see Section 1807.1.2.

- Where unbalanced backfill height exceeds 8 feet and design lateral soil loads from Table 1610.1 are used, the requirements for 30 and 45 psf per foot of depth are not applicable. See Section 1610.

1807.1.6.3.1 Alternative Foundation Wall Reinforcement

In lieu of the reinforcement provisions for masonry foundation walls in Table 1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4), alternative reinforcing bar sizes and spacings having an equivalent cross-sectional area of reinforcement per linear foot (mm) of wall shall be permitted to be used, provided that the spacing of reinforcement does not exceed 72 inches (1829 mm) and reinforcing bar sizes do not exceed No. 11.

1807.1.6.3.2 Seismic Requirements

Based on the seismic design category assigned to the structure in accordance with Section 1613, masonry foundation walls designed using Tables 1807.2.5.

- Seismic Design Categories A and B. No additional seismic requirements.

- Seismic Design Category C. A design using Tables 1807.1.6.3(1) through 1807.1.6.3(4) is subject to the seismic requirements of Section 7.4.3 of TMS 402.

- Seismic Design Category D. A design using Tables 1807.1.6.3(2) through 1807.1.6.3(4) is subject to the seismic requirements of Section 7.4.4 of TMS 402.

- Seismic Design Categories E and F. A design using Tables 1807.1.6.3(2) through 1807.1.6.3(4) is subject to the seismic requirements of Section 7.4.5 of TMS 402.

1807.2 Retaining Walls

Diagram

Retaining walls shall be designed in accordance with Sections 1807.2.1 through 1807.2.4.

UpCodes Diagram (1)

Guards at Retaining Walls

1807.2.1 General

Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and water uplift.

1807.2.2 Design Lateral Soil Loads

Retaining walls shall be designed for the lateral soil loads set forth in Section 1610. [OSHPD 1R, 2 & 5] Retaining wall lateral soil loads determined by a geotechnical investigation report in accordance with Section 1803.5.12 and shall not be less than 80 percent of the lateral soil loads determined in accordance with Section 1610. For use with the load combinations, lateral soil loads due to gravity load surcharge shall be considered gravity loads and seismic earth pressure increases due to earthquake shall be considered as seismic loads. For structures assigned to Seismic Design Category D, E or F, the design of retaining walls supporting more than 6 feet (1829 mm) of backfill height shall incorporate the additional seismic lateral earth pressure in accordance with the geotechnical investigation where required in Section 1803.2.

1807.2.3 Safety Factor

Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605 shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall.

Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.

1807.2.4 Segmental Retaining Walls

Dry-cast concrete units used in the construction of segmental retaining walls shall comply with ASTM C1372.

1807.2.5 Guards

Diagram

Guards shall be provided at retaining walls in accordance with Sections 1807.2.5.1 through 1807.2.5.3.

Exception: Guards are not required at retaining walls not accessible to the public.

UpCodes Diagram (1)

Primary

Guards at Retaining Walls

1807.2.5.1 Where Required

At retaining walls located within 36 inches (914mm) of walking surfaces, a guard shall be required between the walking surface and the open side of the retaining wall where the walking surface is located more than 30 inches (762 mm) measured vertically to the surface or grade below at any point within 36 inches (914mm) horizontally to the edge of the open side. Guards shall comply with Section 1607.9.

1807.2.5.2 Height

Required guards at retaining walls shall comply with the height requirements of Section 1015.3.

1807.2.5.3 Opening Limitations

Required guards shall comply with the opening limitations of Section 1015.4.

1807.3 Embedded Posts and Poles

Designs to resist both axial and lateral loads employing posts or poles as columns embedded in earth or in concrete footings in earth shall be in accordance with Sections 1807.3.1 through 1807.3.3 or ASABE EP 486.3.

1807.3.1 Limitations

The design procedures outlined in this section are subject to the following limitations:

- The frictional resistance for structural walls and slabs on silts and clays shall be limited to one-half of the normal force imposed on the soil by the weight of the footing or slab.

- Posts embedded in earth shall not be used to provide lateral support for structural or nonstructural materials such as plaster, masonry or concrete unless bracing is provided that develops the limited deflection required.

Wood poles shall be treated in accordance with AWPA U1 for sawn timber posts (Commodity Specification A, Use Category 4B) and for round timber posts (Commodity Specification B, Use Category 4B).

1807.3.2 Design Criteria

The depth to resist lateral loads shall be determined using the design criteria established in Sections 1807.3.2.1 through 1807.3.2.3, or by other methods approved by the building official.

1807.3.2.1 Nonconstrained

The following formula shall be used in determining the depth of embedment required to resist lateral loads where lateral constraint is not provided at the ground surface, such as by a rigid floor or rigid ground surface pavement, and where lateral constraint is not provided above the ground surface, such as by a structural diaphragm.

Equation 18-1

where:

A = 2.34P/(S1b).

b = Diameter of round post or footing or diagonal dimension of square post or footing, feet (m).

d = Depth of embedment in earth in feet (m) but not over 12 feet (3658 mm) for purpose of computing lateral pressure.

h = Distance in feet (m) from ground surface to point of application of "P."

P = Applied lateral force in pounds (kN).

S1 = Allowable lateral soil-bearing pressure as set forth in Section 1806.2 based on a depth of one-third the depth of embedment in pounds per square foot (psf) (kPa).

1807.3.2.2 Constrained

The following formula shall be used to determine the depth of embedment required to resist lateral loads where lateral constraint is provided at the ground surface, such as by a rigid floor or slab-on-ground.

Equation 18-2

or alternatively

Equation 18-3

where:

Mg = Moment in the post at grade, in foot-pounds (kN-m).

S3 = Allowable lateral soil-bearing pressure as set forth in Section 1806.2 based on a depth equal to the depth of embedment in pounds per square foot (kPa).

1807.3.2.3 Vertical Load

The resistance to vertical loads shall be determined using the vertical foundation pressure set forth in Table 1806.2.

1807.3.3 Backfill

The backfill in the annular space around columns not embedded in poured footings shall be by one of the following methods:

- Backfill shall be of concrete with a specified compressive strength of not less than 2,000 psi (13.8 MPa). The hole shall be not less than 4 inches (102 mm) larger than the diameter of the column at its bottom or 4 inches (102 mm) larger than the diagonal dimension of a square or rectangular column.

- Backfill shall be of clean sand. The sand shall be thoroughly compacted by tamping in layers not more than 8 inches (203 mm) in depth.

- Backfill shall be of controlled low-strength material (CLSM).

Section 1808 Foundations

1808.1 General

Diagram

Foundations shall be designed and constructed in accordance with Sections 1808.2 through 1808.9. Shallow foundations shall satisfy the requirements of Section 1809. Deep foundations shall satisfy the requirements of Section 1810.

UpCodes Diagrams (2)

Primary

Types of Foundations

Foundation Elevation and Drainage

1808.2 Design for Capacity and Settlement

Foundations shall be so designed that the allowable bearing capacity of the soil is not exceeded, and that differential settlement is minimized. Foundations in areas with expansive soils shall be designed in accordance with the provisions of Section 1808.6.

1808.3 Design Loads

Foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 2.3 or 2.4 of ASCE 7 or the alternative allowable stress design load combinations of Section 1605.2. The dead load is permitted to include the weight of foundations and overlying fill. Reduced live loads, as specified in Sections 1607.13 and 1607.14, shall be permitted to be used in the design of foundations.

1808.3.1 Seismic Overturning

Where foundations are proportioned using the load combinations of Section 2.3 or 2.4 of ASCE 7 and the computation of seismic over-turning effects is by equivalent lateral force analysis or modal analysis, the proportioning shall be in accordance with Section 12.13.4 of ASCE 7.

1808.3.2 Surcharge

Fill or other surcharge loads shall not be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or the surcharge. Existing footings or foundations that will be affected by any excavation shall be underpinned or otherwise protected against settlement and shall be protected against detrimental lateral or vertical movement or both.

Exception: Minor grading for landscaping purposes shall be permitted where done with walk-behind equipment, where the grade is not increased more than 1 foot (305 mm) from original design grade or where approved by the building official.

1808.4 Vibratory Loads

Where machinery operations or other vibrations are transmitted through the foundation, consideration shall be given in the foundation design to prevent detrimental disturbances of the soil.

1808.5 Shifting or Moving Soils

Where it is known that the shallow subsoils are of a shifting or moving character, foundations shall be carried to a sufficient depth to ensure stability.

1808.6 Design for Expansive Soils

Foundations for buildings and structures founded on expansive soils shall be designed in accordance with Section 1808.6.1 or 1808.6.2.

Exceptions: Foundation design need not comply with Section 1808.6.1 or 1808.6.2 where one of the following conditions is satisfied:

- The soil is removed in accordance with Section 1808.6.3.

- The building official approves stabilization of the soil in accordance with Section 1808.6.4.

1808.6.1 Foundations

Foundations placed on or within the active zone of expansive soils shall be designed to resist differential volume changes and to prevent structural damage to the supported structure. Deflection and racking of the supported structure shall be limited to that which will not interfere with the usability and serviceability of the structure.

Foundations placed below where volume change occurs or below expansive soil shall comply with the following provisions:

- Foundations extending into or penetrating expansive soils shall be designed to prevent uplift of the supported structure.

- Foundations penetrating expansive soils shall be designed to resist forces exerted on the foundation due to soil volume changes or shall be isolated from the expansive soil.

1808.6.2 Slab-on-Ground Foundations

Moments, shears and deflections for use in designing slab-on-ground, mat or raft foundations on expansive soils shall be determined in accordance with WRI/CRSI or PTI DC 10.5. Using the moments, shears and deflections determined above, nonprestressed slabs-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with WRI/CRSI and post-tensioned slabs-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with PTI DC 10.5. It shall be permitted to analyze and design such slabs by other methods that account for soil-structure interaction, the deformed shape of the soil support, the plate or stiffened plate action of the slab as well as both center lift and edge lift conditions. Such alternative methods shall be rational and the basis for all aspects and parameters of the method shall be available for peer review.

1808.6.3 Removal of Expansive Soil

Where expansive soil is removed in lieu of designing foundations in accordance with Section 1808.6.1 or 1808.6.2, the soil shall be removed to a depth sufficient to ensure a constant moisture content in the remaining soil. Fill material shall not contain expansive soils and shall comply with Section 1804.5 or 1804.6.

Exception: Expansive soil need not be removed to the depth of constant moisture, provided that the confining pressure in the expansive soil created by the fill and supported structure exceeds the swell pressure.

1808.6.4 Stabilization

Where the active zone of expansive soils is stabilized in lieu of designing foundations in accordance with Section 1808.6.1 or 1808.6.2, the soil shall be stabilized by chemical, dewatering, presaturation or equivalent techniques.

1808.7 Foundations on or Adjacent to Slopes

The placement of buildings and structures on or adjacent to slopes steeper than one unit vertical in three units horizontal (33.3-percent slope) shall comply with Sections 1808.7.1 through 1808.7.5.

1808.7.1 Building Clearance From Ascending Slopes

Diagram

In general, buildings below slopes shall be set a sufficient distance from the slope to provide protection from slope drainage, erosion and shallow failures. Except as provided in Section 1808.7.5 and Figure 1808.7.1, the following criteria will be assumed to provide this protection. Where the existing slope is steeper than one unit vertical in one unit horizontal (100-percent slope), the toe of the slope shall be assumed to be at the intersection of a horizontal plane drawn from the top of the foundation and a plane drawn tangent to the slope at an angle of 45 degrees (0.79 rad) to the horizontal. Where a retaining wall is constructed at the toe of the slope, the height of the slope shall be measured from the top of the wall to the top of the slope.

FIGURE 1808.7.1—FOUNDATION CLEARANCES FROM SLOPES

For SI: 1 foot = 304.8 mm.

UpCodes Diagrams (4)

Primary

Retaining Wall: Setback at Uphill Slope

Primary

Footings: Setback from Ascending Slope

Primary

Footings: Setback from Steep Slope

Primary

Footings: Setbacks from Descending Slope

1808.7.2 Foundation Setback From Descending Slope Surface

Diagram

Foundations on or adjacent to slope surfaces shall be founded in firm material with an embedment and set back from the slope surface sufficient to provide vertical and lateral support for the foundation without detrimental settlement. Except as provided for in Section 1808.7.5 and Figure 1808.7.1, the following setback is deemed adequate to meet the criteria. Where the slope is steeper than 1 unit vertical in 1 unit horizontal (100-percent slope), the required setback shall be measured from an imaginary plane 45 degrees (0.79 rad) to the horizontal, projected upward from the toe of the slope.

UpCodes Diagrams (2)

Primary

Footings: Setback from Steep Slope

Footings: Setbacks from Descending Slope

1808.7.3 Pools

Diagram

The setback between pools regulated by this code and slopes shall be equal to one-half the building footing setback distance required by this section. That portion of the pool wall within a horizontal distance of 7 feet (2134 mm) from the top of the slope shall be capable of supporting the water in the pool without soil support.

UpCodes Diagrams (3)

Primary

Swimming Pools Next to Descending Slopes

Pool Enclosures and Gates

Swimming Pool: Equipotential Bonding (NFPA 70)

1808.7.4 Foundation Elevation

Diagram

On graded sites, the top of any exterior foundation shall extend above the elevation of the street gutter at point of discharge or the inlet of an approved drainage device not less than 12 inches (305 mm) plus 2 percent. Alternate elevations are permitted subject to the approval of the building official, provided that it can be demonstrated that required drainage to the point of discharge and away from the structure is provided at all locations on the site.

UpCodes Diagram (1)

Primary

Foundation Elevation and Drainage

1808.7.5 Alternate Setback and Clearance

Alternate setbacks and clearances are permitted, subject to the approval of the building official. The building official shall be permitted to require a geotechnical investigation as set forth in Section 1803.5.10.

1808.8 Concrete Foundations

Diagram

The design, materials and construction of concrete foundations shall comply with Sections 1808.8.1 through 1808.8.6 and the provisions of Chapter 19.

Exception: [OSHPD 1R, 2 & 5] Not permitted by OSHPD. Where concrete footings supporting walls of light-frame construction are designed in accordance with Table 1809.7, a specific design in accordance with Chapter 19 is not required.

UpCodes Diagram (1)

Example: Steel Column to Conc. Pedestal / Footing

1808.8.1 Concrete or Grout Strength and Mix Proportioning

Concrete or grout in foundations shall have a specified compressive strength (f 'c) not less than the largest applicable value indicated in Table 1808.8.1.

Where concrete or grout is to be pumped, the mix design including slump shall be adjusted to produce a pumpable mixture.

TABLE 1808.8.1—MINIMUM SPECIFIED COMPRESSIVE STRENGTH f 'c OF CONCRETE OR GROUT

| FOUNDATION ELEMENT OR CONDITION | SPECIFIED COMPRESSIVE STRENGTH, f 'c |
| --- | --- |
| 1. Foundations for structures assigned to Seismic Design Category A, B or C [OSHPD 1R, 2 & 5] Not permitted by OSHPD. | 2,500 psi |
| 2a. Foundations for Group R or U occupancies of light-frame construction, two stories or less in height, assigned to Seismic Design Category D, E or F [OSHPD 1R, 2 & 5] Not permitted by OSHPD. | 2,500 psi |
| 2b. Foundations for other structures assigned to Seismic Design Category D, E or F | 3,000 psi |
| 3. Precast nonprestressed driven piles | 4,000 psi |
| 4. Socketed drilled shafts | 4,000 psi |
| 5. Micropiles | 4,000 psi |
| 6. Precast prestressed driven piles | 5,000 psi |

For SI: 1 pound per square inch = 0.00689 MPa.

1808.8.2 Concrete Cover

Diagram

The concrete cover provided for prestressed and nonprestressed reinforcement in foundations shall be not less than the largest applicable value specified in Table 1808.8.2. Longitudinal bars spaced less than 11/2 inches (38 mm) clear distance apart shall be considered to be bundled bars for which the concrete cover provided shall be not less than that required by Section 20.5.1.3.5 of ACI 318. Concrete cover shall be measured from the concrete surface to the outermost surface of the steel to which the cover requirement applies. Where concrete is placed in a temporary or permanent casing or a mandrel, the inside face of the casing or mandrel shall be considered to be the concrete surface.

TABLE 1808.8.2—MINIMUM CONCRETE COVER

| FOUNDATION ELEMENT OR CONDITION | MINIMUM COVER |
| --- | --- |
| 1. Shallow foundations | In accordance with Section 20.5 of ACI 318 |
| 2. Precast nonprestressed deep foundation elements |  |
| Exposed to seawater | 3 inches |
| Not manufactured under plant conditions | 2 inches |
| Manufactured under plant control conditions | In accordance with Section 20.5.1.3.3 of ACI 318 |
| 3. Precast prestressed deep foundation elements |  |
| Exposed to seawater | 2.5 inches |
| Other | In accordance with Section 20.5.1.3.3 of ACI 318 |
| 4. Cast-in-place deep foundation elements not enclosed by a steel pipe, tube or permanent casing | 2.5 inches |
| 5. Cast-in-place deep foundation elements enclosed by a steel pipe, tube or permanent casing | 1 inch |
| 6. Structural steel core within a steel pipe, tube or permanent casing | 2 inches |
| 7. Cast-in-place drilled shafts enclosed by a stable rock socket | 1.5 inches |

For SI:1 inch = 25.4 mm.

UpCodes Diagrams (6)

Primary

Min. Conc. Cover: Cast In Place Deep Foundations

Primary

Min. Conc. Cover: Cased Deep Foundations

Primary

Min. Conc. Cover: Deep Precast Found. Elements

Primary

Min. Conc. Cover: Cast-in-place, Rock Socket

Primary

Min. Conc. Cover: Steel Core in Cased Pier

Min. Conc. Cover: Shallow Foundations

1808.8.3 Placement of Concrete

Concrete shall be placed in such a manner as to ensure the exclusion of any foreign matter and to secure a full-size foundation. Concrete shall not be placed through water unless a tremie or other method approved by the building official is used. Where placed under or in the presence of water, the concrete shall be deposited by approved means to ensure minimum segregation of the mix and negligible turbulence of the water. Where depositing concrete from the top of a deep foundation element, the concrete shall be chuted directly into smooth-sided pipes or tubes or placed in a rapid and continuous operation through a funnel hopper centered at the top of the element.

1808.8.4 Protection of Concrete

Concrete foundations shall be protected from freezing during depositing and for a period of not less than 5 days thereafter. Water shall not be allowed to flow through the deposited concrete.

1808.8.5 Forming of Concrete

Concrete foundations are permitted to be cast against the earth where, in the opinion of the building official, soil conditions do not require formwork. Where formwork is required, it shall be in accordance with Section 26.11 of ACI 318.

1808.8.6 Seismic Requirements

See Section 1905 for additional requirements for foundations of structures assigned to Seismic Design Category C, D, E or F.

For structures assigned to Seismic Design Category C, D, E or F, provisions of Section 18.13 of ACI 318 shall apply where not in conflict with the provisions of Sections 1808 through 1810.

Exception: [OSHPD 1R, 2 & 5] Not permitted by OSHPD. Detached one- and two-family dwellings of light-frame construction and two stories or less above grade plane are not required to comply with the provisions of Section 18.13 of ACI 318.

1808.9 Vertical Masonry Foundation Elements

Vertical masonry foundation elements that are not foundation piers as defined in Section 202 shall be designed as piers, walls or columns, as applicable, in accordance with TMS 402.

Section 1809 Shallow Foundations

Diagram

UpCodes Diagrams (6)

Interior Column on Footing w/o Pier

Frost Protection at Shallow Foundations (Residential)

Example: Steel Column to Conc. Pedestal / Footing

Foundation Plates and Sills

Braced Wall Line Sill Plate Anchorage in SDC D & E

Example: Interior Steel Column to Foundation

1809.1 General

Shallow foundations shall be designed and constructed in accordance with Sections 1809.2 through 1809.13.

1809.2 Supporting Soils

Shallow foundations shall be built on undisturbed soil, compacted fill material or controlled low-strength material (CLSM). Compacted fill material shall be placed in accordance with Section 1804.6. CLSM shall be placed in accordance with Section 1804.7.

1809.3 Stepped Footings

Diagram

The top surface of footings shall be level. The bottom surface of footings shall be permitted to have a slope not exceeding 1 unit vertical in 10 units horizontal (10-percent slope). Footings shall be stepped where it is necessary to change the elevation of the top surface of the footing or where the surface of the ground slopes more than 1 unit vertical in 10 units horizontal (10-percent slope).

[OSHPD 1R, 2 & 5] Individual steps in continuous footings shall not exceed 18 inches (457 mm) in height and the slope of a series of such steps shall not exceed 1 unit vertical to 2 units horizontal (50-percent slope) unless otherwise recommended by a geotechnical report. The steps shall be detailed on the drawings. The local effects due to the discontinuity of the steps shall be considered in the design of the foundation.

UpCodes Diagrams (2)

Primary

Footings: Stepped

Primary

Example: Stepped Footing Reinforcing

1809.4 Depth and Width of Footings

The minimum depth of footings below the undisturbed ground surface shall be 12 inches (305 mm). Where applicable, the requirements of Section 1809.5 shall be satisfied. The minimum width of footings shall be 12 inches (305 mm).

1809.5 Frost Protection

Except where otherwise protected from frost, foundations and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods:

- Extending below the frost line of the locality.

- Constructing in accordance with ASCE 32.

- Erecting on solid rock.

Exception: Free-standing buildings meeting all of the following conditions shall not be required to be protected:

- Assigned to Risk Category I.

- Area of 600 square feet (56 m2) or less for light-frame construction or 400 square feet (37 m2) or less for other than light-frame construction.

- Eave height of 10 feet (3048 mm) or less.

Shallow foundations shall not bear on frozen soil unless such frozen condition is of a permanent character.

1809.5.1 Frost Protection at Required Exits

Frost protection shall be provided at exterior landings for all required exits with outward-swinging doors. Frost protection shall only be required to the extent necessary to ensure the unobstructed opening of the required exit doors.

1809.6 Location of Footings

Footings on granular soil shall be so located that the line drawn between the lower edges of adjacent footings shall not have a slope steeper than 30 degrees (0.52 rad) with the horizontal, unless the material supporting the higher footing is braced or retained or otherwise laterally supported in an approved manner or a greater slope has been properly established by engineering analysis.

1809.7 Prescriptive Footings for Light-Frame Construction

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Where a specific design is not provided, concrete or masonry-unit footings supporting walls of light-frame construction shall be permitted to be designed in accordance with Table 1809.7.

TABLE 1809.7—PRESCRIPTIVE FOOTINGS SUPPORTING WALLS OF LIGHT-FRAME CONSTRUCTIONa, b, c, d, e

| NUMBER OF FLOORS SUPPORTED BY THE FOOTINGf | WIDTH OF FOOTING (inches) | THICKNESS OF FOOTING (inches) |
| --- | --- | --- |
| 1 | 12 | 6 |
| 2 | 15 | 6 |
| 3 | 18 | 8g |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

- Depth of footings shall be in accordance with Section 1809.4.

- The ground under the floor shall be permitted to be excavated to the elevation of the top of the footing.

- Interior stud-bearing walls shall be permitted to be supported by isolated footings. The footing width and length shall be twice the width shown in this table, and footings shall be spaced not more than 6 feet on center.

- See Section 1905 for additional requirements for concrete footings of structures assigned to Seismic Design Category C, D, E or F.

- For thickness of foundation walls, see Section 1807.1.6.

- Footings shall be permitted to support a roof in addition to the stipulated number of floors. Footings supporting roof only shall be as required for supporting one floor.

- Plain concrete footings for Group R-3 occupancies shall be permitted to be 6 inches thick.

1809.8 Plain Concrete Footings

Diagram

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. The edge thickness of plain concrete footings supporting walls of other than light-frame construction shall be not less than 8 inches (203 mm) where placed on soil or rock.

Exception: For plain concrete footings supporting Group R-3 occupancies, the edge thickness is permitted to be 6 inches (152 mm), provided that the footing does not extend beyond a distance greater than the thickness of the footing on either side of the supported wall.

UpCodes Diagram (1)

Prescriptive Foundation Wall and Drain

1809.9 Masonry-Unit Footings

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. The design, materials and construction of masonry-unit footings shall comply with Sections 1809.9.1 and 1809.9.2, and the provisions of Chapter 21.

Exception: Where a specific design is not provided, masonry-unit footings supporting walls of light-frame construction shall be permitted to be designed in accordance with Table 1809.7.

1809.9.1 Dimensions

Masonry-unit footings shall be laid in Type M or S mortar complying with Section 2103.2.1 and the depth shall be not less than twice the projection beyond the wall, pier or column. The width shall be not less than 8 inches (203 mm) wider than the wall supported thereon.

1809.9.2 Offsets

The maximum offset of each course in brick foundation walls stepped up from the footings shall be 11/2 inches (38 mm) where laid in single courses, and 3 inches (76 mm) where laid in double courses.

1809.10 Pier and Curtain Wall Foundations

Except in Seismic Design Categories D, E and F, pier and curtain wall foundations shall be permitted to be used to support light-frame construction not more than two stories above grade plane, provided that the following requirements are met:

- All load-bearing walls shall be placed on continuous concrete footings bonded integrally with the exterior wall footings.

- The minimum actual thickness of a load-bearing masonry wall shall be not less than 4 inches (102 mm) nominal or 35/8 inches (92 mm) actual thickness, and shall be bonded integrally with piers spaced 6 feet (1829 mm) on center (o.c.).

- Piers shall be constructed in accordance with Chapter 21 and the following:

  - The unsupported height of the masonry piers shall not exceed 10 times their least dimension.

  - Where structural clay tile or hollow concrete masonry units are used for piers supporting beams and girders, the cellular spaces shall be filled solidly with concrete or Type M or S mortar.

Exception: Unfilled hollow piers shall be permitted where the unsupported height of the pier is not more than four times its least dimension.

  - Hollow piers shall be capped with 4 inches (102 mm) of solid masonry or concrete or the cavities of the top course shall be filled with concrete or grout.

- The maximum height of a 4-inch (102 mm) load-bearing masonry foundation wall supporting wood frame walls and floors shall not be more than 4 feet (1219 mm) in height.

- The unbalanced fill for 4-inch (102 mm) foundation walls shall not exceed 24 inches (610 mm) for solid masonry, nor 12 inches (305 mm) for hollow masonry.

1809.11 Steel Grillage Footings

Grillage footings of structural steel elements shall be separated with approved steel spacers and be entirely encased in concrete with not less than 6 inches (152 mm) on the bottom and not less than 4 inches (102 mm) at all other points. The spaces between the shapes shall be completely filled with concrete or cement grout.

1809.12 Timber Footings

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Timber footings shall be permitted for buildings of Type V construction and as otherwise approved by the building official. Such footings shall be treated in accordance with AWPA U1 (Commodity Specification A, Use Category 4B). Treated timbers are not required where placed entirely below permanent water level, or where used as capping for wood piles that project above the water level over submerged or marsh lands. The compressive stresses perpendicular to grain in untreated timber footings supported on treated piles shall not exceed 70 percent of the allowable stresses for the species and grade of timber as specified in the ANSI/AWC NDS.

1809.13 Footing Seismic Ties

Where a structure is assigned to Seismic Design Category D, E or F, individual spread footings founded on soil defined in Chapter 20 of ASCE 7 as Site Class E or F shall be interconnected by ties. Unless it is demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade or reinforced concrete slabs on grade, ties shall be capable of carrying, in tension or compression, a force equal to the lesser of the product of the larger footing design gravity load times the seismic coefficient, SDS, divided by 10 and 25 percent of the smaller footing design gravity load.

1809.14 Grade Beams

Grade beams shall comply with the provisions of ACI 318.

Exception: Grade beams not subject to differential settlement exceeding one-fourth of the thresholds specified in ASCE 7 Table 12.13-3 and designed to resist the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 need not comply with ACI 318 Section 18.13.3.1.

1809.15 Pipes and Trenches

[OSHPD 1R, 2 & 5] Unless otherwise recommended by the soils report, open or backfilled trenches parallel with a footing shall not be below a plane having a downward slope of 1 unit vertical to 2 units horizontal (50-percent slope) from a line 9 inches (229 mm) above the bottom edge of the footing, and not closer than 18 inches (457 mm) from the face of such footing.

Where pipes cross under footings, the footings shall be specially designed. Pipe sleeves shall be provided where pipes cross through footings or footing walls and sleeve clearances shall provide for possible footing settlement, but not less than 1 inch (25 mm) all around pipe.

Exception: Alternate trench locations and pipe clearances shall be permitted when approved by registered design professional and the enforcement agent.

Section 1810 Deep Foundations

1810.1 General

Deep foundations shall be analyzed, designed, detailed and installed in accordance with Sections 1810.1 through 1810.4.

1810.1.1 Geotechnical Investigation

Deep foundations shall be designed and installed on the basis of a geotechnical investigation as set forth in Section 1803.

1810.1.2 Use of Existing Deep Foundation Elements

Deep foundation elements left in place where a structure has been demolished shall not be used for the support of new construction unless satisfactory evidence is submitted to the building official, which indicates that the elements are sound and meet the requirements of this code. Such elements shall be load tested or redriven to verify their capacities. The design load applied to such elements shall be the lowest allowable load as determined by tests or redriving data.

1810.1.3 Deep Foundation Elements Classified as Columns

Deep foundation elements standing unbraced in air, water or fluid soils shall be classified as columns and designed as such in accordance with the provisions of this code from their top down to the point where adequate lateral support is provided in accordance with Section 1810.2.1.

Exception: Where the unsupported height to least horizontal dimension of a cast-in-place deep foundation element does not exceed three, it shall be permitted to design and construct such an element as a pedestal in accordance with ACI 318.

1810.1.4 Special Types of Deep Foundations

The use of types of deep foundation elements not specifically mentioned herein is permitted, subject to the approval of the building official, upon the submission of acceptable test data, calculations and other information relating to the structural properties and load capacity of such elements. The allowable stresses for materials shall not in any case exceed the limitations specified herein.

1810.2 Analysis

The analysis of deep foundations for design shall be in accordance with Sections 1810.2.1 through 1810.2.5.

1810.2.1 Lateral Support

Any soil other than fluid soil shall be deemed to afford sufficient lateral support to prevent buckling of deep foundation elements and to permit the design of the elements in accordance with accepted engineering practice and the applicable provisions of this code.

Where deep foundation elements stand unbraced in air, water or fluid soils, it shall be permitted to consider them laterally supported at a point 5 feet (1524 mm) into stiff soil or 10 feet (3048 mm) into soft soil unless otherwise approved by the building official on the basis of a geotechnical investigation by a registered design professional.

1810.2.2 Stability

Deep foundation elements shall be braced to provide lateral stability in all directions. Three or more elements connected by a rigid cap shall be considered to be braced, provided that the elements are located in radial directions from the centroid of the group not less than 60 degrees (1 rad) apart. A two-element group in a rigid cap shall be considered to be braced along the axis connecting the two elements. Methods used to brace deep foundation elements shall be subject to the approval of the building official.

Deep foundation elements supporting walls shall be placed alternately in lines spaced not less than 1 foot (305 mm) apart and located symmetrically under the center of gravity of the wall load carried, unless effective measures are taken to provide for eccentricity and lateral forces, or the foundation elements are adequately braced to provide for lateral stability.

Exceptions:

- Isolated cast-in-place deep foundation elements without lateral bracing shall be permitted where the least horizontal dimension is not less than 2 feet (610 mm), adequate lateral support in accordance with Section 1810.2.1 is provided for the entire height and analysis demonstrates that the element can support the required loads, including mislocations required by Section 1810.3.1.3, with neither harmful distortion nor instability in the structure.

- A single row of deep foundation elements without lateral bracing is permitted for one- and two-family dwellings and lightweight construction not exceeding two stories above grade plane or 35 feet (10 668 mm) in building height, provided that the centers of the elements are located within the width of the supported wall.

1810.2.3 Settlement

The settlement of a single deep foundation element or group thereof shall be estimated based on approved methods of analysis. The predicted settlement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity.

1810.2.4 Lateral Loads

The moments, shears and lateral deflections used for design of deep foundation elements shall be established considering the nonlinear interaction of the shaft and soil, as determined by a registered design professional. Where the ratio of the depth of embedment of the element to its least horizontal dimension is less than or equal to six, it shall be permitted to assume the element is rigid.

1810.2.4.1 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, deep foundation elements on Site Class E or F sites, as determined in Section 1613.2.2, shall be designed and constructed to withstand maximum imposed curvatures from earthquake ground motions and structure response. Curvatures shall include free-field soil strains modified for soil-foundation-structure interaction coupled with foundation element deformations associated with earthquake loads imparted to the foundation by the structure.

Exception: Deep foundation elements that satisfy the following additional detailing requirements shall be deemed to comply with the curvature capacity requirements of this section:

- Precast prestressed concrete piles detailed in accordance with Section 1810.3.8.

- Cast-in-place deep foundation elements with a minimum longitudinal reinforcement ratio of 0.005 extending the full length of the element and detailed in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 as required by Section 1810.3.9.4.2.2.

1810.2.5 Group Effects

The analysis shall include group effects on lateral behavior where the center-to-center spacing of deep foundation elements in the direction of lateral force is less than eight times the least horizontal dimension of an element. The analysis shall include group effects on axial behavior where the center-to-center spacing of deep foundation elements is less than three times the least horizontal dimension of an element. Group effects shall be evaluated using a generally accepted method of analysis; the analysis for uplift of grouped elements with center-to-center spacing less than three times the least horizontal dimension of an element shall be evaluated in accordance with Section 1810.3.3.1.6.

1810.3 Design and Detailing

Deep foundations shall be designed and detailed in accordance with Sections 1810.3.1 through 1810.3.13.

1810.3.1 Design Conditions

Design of deep foundations shall include the design conditions specified in Sections 1810.3.1.1 through 1810.3.1.6, as applicable.

1810.3.1.1 Design Methods for Concrete Elements

Where concrete deep foundations are laterally supported in accordance with Section 1810.2.1 for the entire height and applied forces cause bending moments not greater than those resulting from accidental eccentricities, structural design of the element using the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2 and the allowable stresses specified in this chapter shall be permitted. Otherwise, the structural design of concrete deep foundation elements shall use the strength load combinations specified in ASCE 7, Section 2.3 and approved strength design methods.

1810.3.1.2 Composite Elements

Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section of the composite assembly shall satisfy the applicable requirements of this code, and the maximum allowable load in each section shall be limited by the structural capacity of that section.

1810.3.1.3 Mislocation

The foundation or superstructure shall be designed to resist the effects of the mislocation of any deep foundation element by not less than 3 inches (76 mm). To resist the effects of mislocation, compressive overload of deep foundation elements to 110 percent of the allowable design load shall be permitted.

1810.3.1.4 Driven Piles

Driven piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.

1810.3.1.5 Helical Piles

Helical piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by installation into the ground and service loads.

1810.3.1.5.1 Helical Piles Seismic Requirements

[OSHPD 1R, 2 & 5] For structures assigned to Seismic Design Category D, E or F, capacities of helical piles shall be determined in accordance with Section 1810.3.3 by at least two project specific pre-production tests for each soil profile, size and depth of helical pile. At least two percent of all production piles shall be proof tested to design strength determined by using load combinations in ASCE 7, Section 2.3.6.

Helical piles shall satisfy corrosion resistance requirements of ICC-ES AC 358. In addition, all helical pile materials that are subject to corrosion shall include at least 1/16 inch corrosion allowance.

Helical piles shall not be considered as carrying any horizontal loads.

1810.3.1.6 Casings

Temporary and permanent casings shall be of steel and shall be sufficiently strong to resist collapse and sufficiently watertight to exclude any foreign materials during the placing of concrete. Where a permanent casing is considered reinforcing steel, the steel shall be protected under the conditions specified in Section 1810.3.2.5. Horizontal joints in the casing shall be spliced in accordance with Section 1810.3.6.

1810.3.2 Materials

The materials used in deep foundation elements shall satisfy the requirements of Sections 1810.3.2.1 through 1810.3.2.8, as applicable.

1810.3.2.1 Concrete

Where concrete is cast in a steel pipe or where an enlarged base is formed by compacting concrete, the maximum size for coarse aggregate shall be 3/4 inch (19.1 mm). Concrete to be compacted shall have a zero slump.

1810.3.2.1.1 Seismic Hooks

For structures assigned to Seismic Design Category C, D, E or F, the ends of hoops, spirals and ties used in concrete deep foundation elements shall be terminated with seismic hooks, as defined in ACI 318, and shall be turned into the confined concrete core.

1810.3.2.1.2 ACI 318 Equation (25.7.3.3)

Where this chapter requires detailing of concrete deep foundation elements in accordance with Section 18.7.5.4 of ACI 318, compliance with Equation (25.7.3.3) of ACI 318 shall not be required.

1810.3.2.2 Prestressing Steel

Prestressing steel shall conform to ASTM A416.

1810.3.2.3 Steel

Structural steel H-piles and structural steel sheet piling shall conform to the material requirements in ASTM A6. Steel pipe piles shall conform to the material requirements in ASTM A252. Fully welded steel piles shall be fabricated from plates that conform to the material requirements in ASTM A36, ASTM A283, ASTM A572, ASTM A588 or ASTM A690.

1810.3.2.4 Timber

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Timber deep foundation elements shall be designed as piles or poles in accordance with ANSI/AWC NDS. Round timber elements shall conform to ASTM D25. Sawn timber elements shall conform to DOC PS-20.

1810.3.2.4.1 Preservative Treatment

Timber deep foundation elements used to support permanent structures shall be treated in accordance with this section unless it is established that the tops of the untreated timber elements will be below the lowest ground-water level assumed to exist during the life of the structure. Preservative and minimum final retention shall be in accordance with AWPA U1 (Commodity Specification E, Use Category 4C) for round timber elements and AWPA U1 (Commodity Specification A, Use Category 4B) for sawn timber elements. Preservative-treated timber elements shall be subject to a quality control program administered by an approved agency. Element cutoffs shall be treated in accordance with AWPA M4.

1810.3.2.5 Protection of Materials

Where boring records or site conditions indicate possible deleterious action on the materials used in deep foundation elements because of soil constituents, changing water levels or other factors, the elements shall be adequately protected by materials, methods or processes approved by the building official. Protective materials shall be applied to the elements so as not to be rendered ineffective by installation. The effectiveness of such protective measures for the particular purpose shall have been thoroughly established by satisfactory service records or other evidence.

1810.3.2.6 Allowable Stresses

The allowable stresses for materials used in deep foundation elements shall not exceed those specified in Table 1810.3.2.6.

TABLE 1810.3.2.6—ALLOWABLE STRESSES FOR MATERIALS USED IN DEEP FOUNDATION ELEMENTS

| MATERIAL TYPE AND CONDITION | MAXIMUM ALLOWABLE STRESSa |
| --- | --- |
| 1. Concrete or grout in compressionb |  |
| Cast-in-place with a permanent casing in accordance with Section 1810.3.2.7 or Section 1810.3.5.3.4 | 0.4 f'c |
| Cast-in-place in other permanent casing or rock | 0.33 f'c |
| Cast-in-place without a permanent casing | 0.3 f'c |
| Precast nonprestressed | 0.33 f 'c |
| Precast prestressed | 0.33 f'c - 0.27fpc |
| 2. Nonprestressed reinforcement in compression | 0.4 fy ≤ 30,000 psi |
| 3. Steel in compression |  |
| Cores within concrete-filled pipes or tubes | 0.5 Fy ≤ 32,000 psi |
| Pipes, tubes or H-piles, where justified in accordance with Section 1810.3.2.8 | 0.5 Fy ≤ 32,000 psi |
| Pipes or tubes for micropiles | 0.4 Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35 Fy ≤ 24,000 |
| Helical piles | 0.6 Fy ≤ 0.5 Fu |
| 4. Nonprestressed reinforcement in tension |  |
| Within micropiles | 0.6 fy |
| Other conditions |  |
| For load combinations that do not include wind or seismic loads | 0.5 fy ≤ 30,000 psi |
| For load combinations that include wind or seismic loads | 0.5 fy ≤ 40,000 psi |
| 5. Steel in tension |  |
| Pipes, tubes or H-piles, where justified in accordance with Section 1810.3.2.8 | 0.5 Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35 Fy ≤ 24,000 psi |
| Helical piles | 0.6 Fy ≤ 0.5 Fu |
| 6. Timber | In accordance with the ANSI/AWC NDS |

- f 'c is the specified compressive strength of the concrete or grout; fpc is the compressive stress on the gross concrete section due to effective prestress forces only; fy is the specified yield strength of reinforcement; Fy is the specified minimum yield stress of steel; Fu is the specified minimum tensile stress of structural steel.

- The stresses specified apply to the gross cross-sectional area of the concrete for precast prestressed piles and to the net cross-sectional area for all other piles. Where a temporary or permanent casing is used, the inside face of the casing shall be considered the outer edge of the concrete cross-section.

1810.3.2.7 Increased Allowable Compressive Stress for Cased Mandrel-Driven Cast-in-Place Elements

The allowable compressive stress in the concrete shall be permitted to be increased as specified in Table 1810.3.2.6 for those portions of permanently cased cast-in-place elements that satisfy all of the following conditions:

- The design shall not use the casing to resist any portion of the axial load imposed.

- The casing shall have a sealed tip and be mandrel driven.

- The thickness of the casing shall be not less than manufacturer's standard gage No. 14 (0.068 inch) (1.75 mm).

- The casing shall be seamless or provided with seams of strength equal to the basic material and be of a configuration that will provide confinement to the cast-in-place concrete.

- The ratio of steel yield strength (Fy) to specified compressive strength (f 'c) shall be not less than six.

- The nominal diameter of the element shall not be greater than 16 inches (406 mm).

1810.3.2.8 Justification of Higher Allowable Stresses

Use of allowable stresses in Table 1810.3.2.6 that must be justified in accordance with this section shall be permitted where supporting data justifying such higher stresses is submitted to and approved by the building official. Such substantiating data shall include the following:

- A geotechnical investigation in accordance with Section 1803.

- Load tests in accordance with Section 1810.3.3.1.2, regardless of the load supported by the element.

The design and installation of the deep foundation elements shall be under the direct supervision of a registered design professional knowledgeable in the field of soil mechanics and deep foundations who shall submit a report to the building official stating that the elements as installed satisfy the design criteria.

1810.3.3 Determination of Allowable Loads

The allowable axial and lateral loads on deep foundation elements shall be determined by an approved formula, load tests or method of analysis.

1810.3.3.1 Allowable Axial Load

The allowable axial load on a deep foundation element shall be determined in accordance with Sections 1810.3.3.1.1 through 1810.3.3.1.9.

Exception: Where approved by the building official, load testing is not required.

1810.3.3.1.1 Driving Criteria

The allowable compressive load on any driven deep foundation element where determined by the application of an approved driving formula shall not exceed 40 tons (356 kN). For allowable loads above 40 tons (356 kN), the wave equation method of analysis shall be used to estimate driveability for both driving stresses and net displacement per blow at the ultimate load. Allowable loads shall be verified by load tests in accordance with Section 1810.3.3.1.2. The formula or wave equation load shall be determined for gravity-drop or power-actuated hammers and the hammer energy used shall be the maximum consistent with the size, strength and weight of the driven elements. The use of a follower is permitted only with the approval of the building official. The introduction of fresh hammer cushion or pile cushion material just prior to final penetration is not permitted.

1810.3.3.1.2 Load Tests

Where design compressive loads are greater than those determined using the allowable stresses specified in Section 1810.3.2.6, where the design load for any deep foundation element is in doubt, or where cast-in-place deep foundation elements have an enlarged base formed either by compacting concrete or by driving a precast base, control test elements shall be tested in accordance with ASTM D1143 or ASTM D4945. One element or more shall be load tested in each area of uniform subsoil conditions. Where required by the building official, additional elements shall be load tested where necessary to establish the safe design capacity. The resulting allowable loads shall not be more than one-half of the ultimate axial load capacity of the test element as assessed by one of the published methods listed in Section 1810.3.3.1.3 with consideration for the test type, duration and subsoil. The ultimate axial load capacity shall be determined by a registered design professional with consideration given to tolerable total and differential settlements at design load in accordance with Section 1810.2.3. In subsequent installation of the balance of deep foundation elements, all elements shall be deemed to have a supporting capacity equal to that of the control element where such elements are of the same type, size and relative length as the test element; are installed using the same or comparable methods and equipment as the test element; are installed in similar subsoil conditions as the test element; and, for driven elements, where the rate of penetration (for example, net displacement per blow) of such elements is equal to or less than that of the test element driven with the same hammer through a comparable driving distance.

1810.3.3.1.3 Load Test Evaluation Methods

It shall be permitted to evaluate load tests of deep foundation elements using any of the following methods:

- Davisson Offset Limit.

- Brinch-Hansen 90-percent Criterion.

- Butler-Hoy Criterion.

- Other methods approved by the building official.

1810.3.3.1.4 Allowable Shaft Resistance

The assumed shaft resistance developed by any uncased cast-in-place deep foundation element shall not exceed one-sixth of the bearing value of the soil material at minimum depth as set forth in Table 1806.2, up to 500 psf (24 kPa), unless a greater value is allowed by the building official on the basis of a geotechnical investigation as specified in Section 1803 or a greater value is substantiated by a load test in accordance with Section 1810.3.3.1.2. Shaft resistance and end-bearing resistance shall not be assumed to act simultaneously unless determined by a geotechnical investigation in accordance with Section 1803.

1810.3.3.1.5 Uplift Capacity of a Single Deep Foundation Element

Where required by the design, the uplift capacity of a single deep foundation element shall be determined by an approved method of analysis based on a minimum factor of safety of three or by load tests conducted in accordance with ASTM D3689. The maximum allowable uplift load shall not exceed the ultimate load capacity as determined in Section 1810.3.3.1.2, using the results of load tests conducted in accordance with ASTM D3689, divided by a factor of safety of two.

Exception: Where uplift is due to wind or seismic loading, the minimum factor of safety shall be two where capacity is determined by an analysis and one and one-half where capacity is determined by load tests.

1810.3.3.1.6 Allowable Uplift Load of Grouped Deep Foundation Elements

For grouped deep foundation elements subjected to uplift, the allowable uplift load for the group shall be calculated by a generally accepted method of analysis. Where the deep foundation elements in the group are placed at a center-to-center spacing less than three times the least horizontal dimension of the largest single element, the allowable uplift load for the group is permitted to be calculated as the lesser of:

- The proposed individual allowable uplift load times the number of elements in the group.

- Two-thirds of the effective weight of the group and the soil contained within a block defined by the perimeter of the group and the length of the element, plus two-thirds of the ultimate shear resistance along the soil block.

1810.3.3.1.7 Load-Bearing Capacity

Deep foundation elements shall develop ultimate load capacities of not less than twice the design working loads in the designated load-bearing layers. Analysis shall show that soil layers underlying the designated load-bearing layers do not cause the load-bearing capacity safety factor to be less than two.

1810.3.3.1.8 Bent Deep Foundation Elements

The load-bearing capacity of deep foundation elements discovered to have a sharp or sweeping bend shall be determined by an approved method of analysis or by load testing a representative element.

1810.3.3.1.9 Helical Piles

The allowable axial design load, Pa, of helical piles shall be determined as follows:

Equation 18-4

where Pu is the least value of:

1. Base capacity plus shaft resistance of the helical pile. The base capacity is equal to the sum of the areas of the helical bearing plates times the ultimate bearing capacity of the soil or rock comprising the bearing stratum. The shaft resistance is equal to the area of the shaft above the uppermost helical bearing plate times the ultimate skin resistance.

2. Ultimate capacity determined from well-documented correlations with installation torque.

3. Ultimate capacity determined from load tests where required by Section 1810.3.3.1.2. [OSHPD 1R, 2 & 5] Load tests are required to determine the ultimate capacity.

4. Ultimate axial capacity of pile shaft.

5. Ultimate axial capacity of pile shaft couplings.

6. Sum of the ultimate axial capacity of helical bearing plates affixed to pile.

1810.3.3.2 Allowable Lateral Load

Where required by the design, the lateral load capacity of a single deep foundation element or a group thereof shall be determined by an approved method of analysis or by lateral load tests to not less than twice the proposed design working load. The resulting allowable lateral load shall not be more than one-half of the load that produces a gross lateral movement of 1 inch (25 mm) at the lower of the top of the foundation element and the ground surface, unless it can be shown that the predicted lateral movement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity. Group effects shall be evaluated where required by Section 1810.2.5.

1810.3.4 Subsiding Soils or Strata

Where deep foundation elements are installed through subsiding soils or other subsiding strata and derive support from underlying firmer materials, consideration shall be given to the downward frictional forces potentially imposed on the elements by the subsiding upper strata.

Where the influence of subsiding soils or strata is considered as imposing loads on the element, the allowable stresses specified in this chapter shall be permitted to be increased where satisfactory substantiating data are submitted.

1810.3.5 Dimensions of Deep Foundation Elements

The dimensions of deep foundation elements shall be in accordance with Sections 1810.3.5.1 through 1810.3.5.3, as applicable.

1810.3.5.1 Precast

The minimum lateral dimension of precast concrete deep foundation elements shall be 8 inches (203 mm). Corners of square elements shall be chamfered.

1810.3.5.2 Cast-in-Place or Grouted-in-Place

Cast-in-place and grouted-in-place deep foundation elements shall satisfy the requirements of this section.

1810.3.5.2.1 Cased

Cast-in-place or grouted-in-place deep foundation elements with a permanent casing shall have a nominal outside diameter of not less than 8 inches (203 mm).

1810.3.5.2.2 Uncased

Cast-in-place or grouted-in-place deep foundation elements without a permanent casing shall have a specified diameter of not less than 12 inches (305 mm). The element length shall not exceed 30 times the specified diameter.

Exception: The length of the element is permitted to exceed 30 times the specified diameter, provided that the design and installation of the deep foundations are under the direct supervision of a registered design professional knowledgeable in the field of soil mechanics and deep foundations. The registered design professional shall submit a report to the building official stating that the elements were installed in compliance with the approved construction documents.

1810.3.5.2.3 Micropiles

Micropiles shall have a nominal diameter of 12 inches (305 mm) or less. The minimum diameter set forth elsewhere in Section 1810.3.5 shall not apply to micropiles.

1810.3.5.3 Steel

Steel deep foundation elements shall satisfy the requirements of this section.

1810.3.5.3.1 Structural Steel H-Piles

Sections of structural steel H-piles shall comply with the requirements for HP shapes in ASTM A6, or the following:

- The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall be not less than 80 percent of the depth of the section.

- The nominal depth in the direction of the web shall be not less than 8 inches (203 mm).

- Flanges and web shall have a minimum nominal thickness of 3/8 inch (9.5 mm).

For structures assigned to Seismic Design Category D, E or F, design and detailing of H-piles shall also conform to the requirements of AISC 341.

1810.3.5.3.2 Fully Welded Steel Piles Fabricated From Plates

Sections of fully welded steel piles fabricated from plates shall comply with the following:

- The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall be not less than 80 percent of the depth of the section.

- The nominal depth in the direction of the web shall be not less than 8 inches (203 mm).

- Flanges and web shall have a minimum nominal thickness of 3/8 inch (9.5 mm).

1810.3.5.3.3 Structural Steel Sheet Piling

Individual sections of structural steel sheet piling shall conform to the profile indicated by the manufacturer, and shall conform to the general requirements specified by ASTM A6.

[OSHPD 1R, 2 & 5] Installation of sheet piling shall satisfy inspection, monitoring and observation requirements in Sections 1812.6 and 1812.7.

1810.3.5.3.4 Steel Pipes and Tubes

Steel pipes and tubes used as deep foundation elements shall have a nominal outside diameter of not less than 8 inches (203 mm). Where steel pipes or tubes are driven open ended, they shall have not less than 0.34 square inch (219 mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 Nm) of pile hammer energy, or shall have the equivalent strength for steels having a yield strength greater than 35,000 psi (241 MPa) or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the pile section is appropriate for the selected hammer. Where a pipe or tube with wall thickness less than 0.179 inch (4.6 mm) is driven open ended, a suitable cutting shoe shall be provided. Concrete-filled steel pipes or tubes in structures assigned to Seismic Design Category C, D, E or F shall have a wall thickness of not less than 3/16 inch (5 mm). The pipe or tube casing for socketed drilled shafts shall have a nominal outside diameter of not less than 18 inches (457 mm), a wall thickness of not less than 3/8 inch (9.5 mm) and a suitable steel driving shoe welded to the bottom; the diameter of the rock socket shall be approximately equal to the inside diameter of the casing.

Exceptions:

- There is no minimum diameter for steel pipes or tubes used in micropiles.

- For mandrel-driven pipes or tubes, the minimum wall thickness shall be 1/10 inch (2.5 mm).

1810.3.5.3.5 Helical Piles

Dimensions of the central shaft and the number, size and thickness of helical bearing plates shall be sufficient to support the design loads.

1810.3.6 Splices

Splices shall be constructed so as to provide and maintain true alignment and position of the component parts of the deep foundation element during installation and subsequent thereto and shall be designed to resist the axial and shear forces and moments occurring at the location of the splice during driving and for design load combinations. Where deep foundation elements of the same type are being spliced, splices shall develop not less than 50 percent of the bending strength of the weaker section. Where deep foundation elements of different materials or different types are being spliced, splices shall develop the full compressive strength and not less than 50 percent of the tension and bending strength of the weaker section. Where structural steel cores are to be spliced, the ends shall be milled or ground to provide full contact and shall be full-depth welded.

Exception: For buildings assigned to Seismic Design Category A or B, splices need not comply with the 50- percent tension and bending strength requirements where justified by supporting data.

Splices occurring in the upper 10 feet (3048 mm) of the embedded portion of an element shall be designed to resist at allowable stresses the moment and shear that would result from an assumed eccentricity of the axial load of 3 inches (76 mm), or the element shall be braced in accordance with Section 1810.2.2 to other deep foundation elements that do not have splices in the upper 10 feet (3048 mm) of embedment.

1810.3.6.1 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F splices of deep foundation elements shall develop the lesser of the following:

- The nominal strength of the deep foundation element.

- The axial and shear forces and moments from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

1810.3.7 Top of Element Detailing at Cutoffs

Where a minimum length for reinforcement or the extent of closely spaced confinement reinforcement is specified at the top of a deep foundation element, provisions shall be made so that those specified lengths or extents are maintained after cutoff.

1810.3.8 Precast Concrete Piles

Precast concrete piles shall be designed and detailed in accordance with ACI 318.

Exceptions:

- For precast prestressed piles in Seismic Design Category C, the minimum volumetric ratio of spirals or circular hoops required by Section 18.13.5.10.4 of ACI 318 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 or Section 2.4.5 and the applicable overstrength factor, Ω0. In such cases, minimum transverse reinforcement index shall be as specified in Section 13.4.5.6 of ACI 318. [OSHPD 1R, 2 & 5] not permitted by OSHPD.

- For precast prestressed piles in Seismic Design Categories D through F and in Site Class A, B, BC, C, CD, D or DE sites, the minimum volumetric ratio of spirals or circular hoops required by Section 18.13.5.10.5(c) of ACI 318 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 or Section 2.4.5 and the applicable overstrength factor, Ω0. In such cases, minimum transverse reinforcement shall be as specified in Section 13.4.5.6 of ACI 318. [OSHPD 1R, 2 & 5] not permitted by OSHPD.

  - [OSHPD 1R, 2 & 5] Exception: Where the axial load from seismic forces is amplified by the applicable overstrength factor, Ω0, the axial load limits in Section 18.13.5.10.6 of ACI 318 may be increased by two times.

1810.3.9 Cast-in-Place Deep Foundations

Cast-in-place deep foundation elements shall be designed and detailed in accordance with Sections 1810.3.9.1 through 1810.3.9.6.

1810.3.9.1 Design Cracking Moment

The design cracking moment (φMn) for a cast-in-place deep foundation element not enclosed by a structural steel pipe or tube shall be determined using the following equation:

Equation 18-5

where:

f 'c = Specified compressive strength of concrete or grout, psi (MPa).

Sm = Elastic section modulus, neglecting reinforcement and casing, cubic inches (mm3).

1810.3.9.2 Required Reinforcement

Where subject to uplift or where the required moment strength determined using the load combinations of ASCE 7, Section 2.3 exceeds the design cracking moment determined in accordance with Section 1810.3.9.1, cast-in-place deep foundations not enclosed by a structural steel pipe or tube shall be reinforced. Where reinforcement is required, it shall be in compliance with Chapter 20 of ACI 318.

1810.3.9.3 Placement of Reinforcement

Reinforcement where required shall be assembled and tied together and shall be placed in the deep foundation element as a unit before the reinforced portion of the element is filled with concrete.

Exceptions:

- Steel dowels embedded 5 feet (1524 mm) or less shall be permitted to be placed after concreting, while the concrete is still in a semifluid state.

- For deep foundation elements installed with a hollow-stem auger, tied reinforcement shall be placed after elements are concreted, while the concrete is still in a semifluid state. Longitudinal reinforcement without lateral ties shall be placed either through the hollow stem of the auger prior to concreting or after concreting, while the concrete is still in a semifluid state.

- For Group R-3 and U occupancies not exceeding two stories of light-frame construction, reinforcement is permitted to be placed after concreting, while the concrete is still in a semifluid state, and the concrete cover requirement is permitted to be reduced to 2 inches (51 mm), provided that the construction method can be demonstrated to the satisfaction of the building official.

1810.3.9.4 Seismic Reinforcement

Where a structure is assigned to Seismic Design Category C, reinforcement shall be provided in accordance with Section 1810.3.9.4.1. Where a structure is assigned to Seismic Design Category D, E or F, reinforcement shall be provided in accordance with Section 1810.3.9.4.2.

Exceptions:

- Isolated deep foundation elements supporting posts of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where detailed so the element is not subject to lateral loads and the soil provides adequate lateral support in accordance with Section 1810.2.1.

- Isolated deep foundation elements supporting posts and bracing from decks and patios appurtenant to Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where the lateral load, E, to the top of the element does not exceed 200 pounds (890 N) and the soil provides adequate lateral support in accordance with Section 1810.2.1.

- Deep foundation elements supporting the concrete foundation wall of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than two No. 4 bars, without ties or spirals, where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations with overstrength factor in Section 2.3.6 or 2.4.5 of ASCE 7 and the soil provides adequate lateral support in accordance with Section 1810.2.1.

- Closed ties or spirals where required by Section 1810.3.9.4.2 shall be permitted to be limited to the top 3 feet (914 mm) of deep foundation elements 10 feet (3048 mm) or less in depth supporting Group R-3 and U occupancies of Seismic Design Category D, not exceeding two stories of light-frame construction.

1810.3.9.4.1 Seismic Reinforcement in Seismic Design Category C

For structures assigned to Seismic Design Category C, cast-in-place deep foundation elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis.

Not fewer than four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.0025, shall be provided throughout the minimum reinforced length of the element as defined in this section starting at the top of the element. The minimum reinforced length of the element shall be taken as the greatest of the following:

- One-third of the element length.

- A distance of 10 feet (3048 mm).

- Three times the least element dimension.

- The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations of ASCE 7, Section 2.3.

Transverse reinforcement shall consist of closed ties or spirals with a minimum 3/8 inch (9.5 mm) diameter. Spacing of transverse reinforcement shall not exceed the smaller of 6 inches (152 mm) or 8-longitudinal-bar diameters, within a distance of three times the least element dimension from the bottom of the pile cap. Spacing of transverse reinforcement shall not exceed 16 longitudinal bar diameters throughout the remainder of the reinforced length.

Exceptions:

- The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes.

- A spiral-welded metal casing of a thickness not less than the manufacturer's standard No. 14 gage (0.068 inch) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.

1810.3.9.4.2 Seismic Reinforcement in Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, cast-in-place deep foundation elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis.

Not fewer than four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.005, shall be provided throughout the minimum reinforced length of the element as defined in this section starting at the top of the element. The minimum reinforced length of the element shall be taken as the greatest of the following:

- One-half of the element length.

- A distance of 10 feet (3048 mm).

- Three times the least element dimension.

- The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations of ASCE 7, Section 2.3.

Transverse reinforcement shall consist of closed ties or spirals not smaller than No. 3 bars for elements with a least dimension up to 20 inches (508 mm), and No. 4 bars for larger elements. Throughout the remainder of the reinforced length outside the regions with transverse confinement reinforcement, as specified in Section 1810.3.9.4.2.1 or 1810.3.9.4.2.2, the spacing of transverse reinforcement shall not exceed the least of the following:

- 12 longitudinal bar diameters.

- One-half the least dimension of the element.

- 12 inches (305 mm).

Exceptions:

- The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes.

- A spiral-welded metal casing of a thickness not less than manufacturer's standard No. 14 gage (0.068 inch) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.

1810.3.9.4.2.1 Site Classes A Through DE

For Site Class A, B, BC, C, CD, D or DE sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within three times the least element dimension of the bottom of the pile cap. A transverse spiral reinforcement ratio of not less than one-half of that required in Table 18.10.6.4(g) of ACI 318 shall be permitted.

1810.3.9.4.2.2 Site Classes E and F

For Site Class E or F sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within seven times the least element dimension of the pile cap and within seven times the least element dimension of the interfaces of strata that are hard or stiff and strata that are liquefiable or are composed of soft- to medium-stiff clay.

1810.3.9.5 Belled Drilled Shafts

Where drilled shafts are belled at the bottom, the edge thickness of the bell shall be not less than that required for the edge of footings. Where the sides of the bell slope at an angle less than 60 degrees (1 rad) from the horizontal, the effects of vertical shear shall be considered.

1810.3.9.6 Socketed Drilled Shafts

Socketed drilled shafts shall have a permanent pipe or tube casing that extends down to bedrock and an uncased socket drilled into the bedrock, both filled with concrete. Socketed drilled shafts shall have reinforcement or a structural steel core for the length as indicated by an approved method of analysis.

The depth of the rock socket shall be sufficient to develop the full load-bearing capacity of the element with a minimum safety factor of two, but the depth shall be not less than the outside diameter of the pipe or tube casing. The design of the rock socket is permitted to be predicated on the sum of the allowable load-bearing pressure on the bottom of the socket plus bond along the sides of the socket.

Where a structural steel core is used, the gross cross-sectional area of the core shall not exceed 25 percent of the gross area of the drilled shaft.

1810.3.10 Micropiles

Micropiles shall be designed and detailed in accordance with Sections 1810.3.10.1 through 1810.3.10.4.

1810.3.10.1 Construction

Micropiles shall develop their load-carrying capacity by means of a bond zone in soil, bedrock or a combination of soil and bedrock. Micropiles shall be grouted and have either a steel pipe or tube or steel reinforcement at every section along the length. It shall be permitted to transition from deformed reinforcing bars to steel pipe or tube reinforcement by extending the bars into the pipe or tube section by not less than their development length in tension in accordance with ACI 318.

1810.3.10.2 Materials

Reinforcement shall consist of deformed reinforcing bars in accordance with ASTM A615 Grade 60 or 75 or ASTM A722 Grade 150.

The steel pipe or tube shall have a minimum wall thickness of 3/16 inch (4.8 mm). Splices shall comply with Section 1810.3.6. The steel pipe or tube shall have a minimum yield strength of 45,000 psi (310 MPa) and a minimum elongation of 15 percent as shown by mill certifications or two coupon test samples per 40,000 pounds (18 160 kg) of pipe or tube.

1810.3.10.3 Reinforcement

For micropiles or portions thereof grouted inside a temporary or permanent casing or inside a hole drilled into bedrock or a hole drilled with grout, the steel pipe or tube or steel reinforcement shall be designed to carry not less than 40 percent of the design compression load. Micropiles or portions thereof grouted in an open hole in soil without temporary or permanent casing and without suitable means of verifying the hole diameter during grouting shall be designed to carry the entire compression load in the reinforcing steel. Where a steel pipe or tube is used for reinforcement, the portion of the grout enclosed within the pipe is permitted to be included in the determination of the allowable stress in the grout.

1810.3.10.4 Seismic Reinforcement

For structures assigned to Seismic Design Category C, a permanent steel casing shall be provided from the top of the micropile down to the point of zero curvature. For structures assigned to Seismic Design Category D, E or F, the micropile shall be considered as an alternative system in accordance with Section 104.2.3 or 1.8.7, as applicable. The alternative system design, supporting documentation and test data shall be submitted to the building official for review and approval.

1810.3.10.4.1 Seismic Requirements

[OSHPD 1R, 2 & 5] For structures assigned to Seismic Design Category D, E or F, a permanent steel casing having a minimum thickness of 3/8 inch shall be provided from the top of the micropile down to a minimum of 120 percent of the point of zero curvature. Capacity of micropiles shall be determined in accordance with Section 1810.3.3 by at least two project specific pre-production tests for each soil profile, size and depth of micropile. At least two percent of all production piles shall be proof tested to design strength determined by using load combinations in ASCE 7, Section 2.3.6.

Steel casing length in soil shall be considered as unbonded and shall not be considered as contributing to friction. Casing shall provide confinement at least equivalent to hoop reinforcing required by ACI 318 Section 18.13.5.

Reinforcement shall have Class 1 corrosion protection in accordance with PTI Recommendations for Prestressed Rock and Soil Anchors. Steel casing design shall include at least 1/16-inch corrosion allowance.

Micropiles shall not be considered as carrying any horizontal loads.

1810.3.11 Pile Caps

Pile caps shall conform with ACI 318 and this section. Pile caps shall be of reinforced concrete, and shall include all elements to which vertical deep foundation elements are connected, including grade beams and mats. The soil immediately below the pile cap shall not be considered as carrying any vertical load, with the exception of a combined pile raft. [OSHPD 1R, 2 & 5] A combined pile raft foundation shall be an alternative system. The tops of vertical deep foundation elements shall be embedded not less than 3 inches (76 mm) into pile caps and the caps shall extend not less than 4 inches (102 mm) beyond the edges of the elements. The tops of elements shall be cut or chipped back to sound material before capping.

1810.3.11.1 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F, concrete deep foundation elements shall be connected to the pile cap in accordance with ACI 318.

For resistance to uplift forces, anchorage of steel pipes, tubes or H-piles to the pile cap shall be made by means other than concrete bond to the bare steel section. Concrete-filled steel pipes or tubes shall have reinforcement of not less than 0.01 times the cross-sectional area of the concrete fill developed into the cap and extending into the fill a length equal to two times the required cap embedment, but not less than the development length in tension of the reinforcement.

1810.3.11.2 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, deep foundation element resistance to uplift forces or rotational restraint shall be provided by anchorage into the pile cap, designed considering the combined effect of axial forces due to uplift and bending moments due to fixity to the pile cap. Anchorage shall develop not less than 25 percent of the strength of the element in tension. Anchorage into the pile cap shall comply with the following:

- In the case of uplift, the anchorage shall be capable of developing the least of the following:

  - The nominal tensile strength of the longitudinal reinforcement in a concrete element.

  - The nominal tensile strength of a steel element.

  - The frictional force developed between the element and the soil multiplied by 1.3.

Exception: The anchorage is permitted to be designed to resist the axial tension force resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

- In the case of rotational restraint, the anchorage shall be designed to resist the axial and shear forces, and moments resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 or the anchorage shall be capable of developing the full axial, bending and shear nominal strength of the element.

- The connection between the pile cap and the steel H-piles or unfilled steel pipe piles in structures assigned to Seismic Design Category D, E or F shall be designed for a tensile force of not less than 10 percent of the pile compression capacity.

Exceptions:

  - Connection tensile capacity need not exceed the strength required to resist seismic load effects including overstrength of ASCE 7 Section 12.4.3 or 12.14.3.2.

  - Connections need not be provided where the foundation or supported structure does not rely on the tensile capacity of the piles for stability under the design seismic force. [OSHPD 1R, 2 & 5] Not permitted by OSHPD.

Where the vertical lateral-force-resisting elements are columns, the pile cap flexural strengths shall exceed the column flexural strength. The connection between batter piles and pile caps shall be designed to resist the nominal strength of the pile acting as a short column. Batter piles and their connection shall be designed to resist forces and moments that result from the application of seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

1810.3.12 Grade Beams

Grade beams shall comply with the provisions of ACI 318.

Exception: Grade beams not subject to differential settlement exceeding one-fourth of the thresholds specified in ASCE 7 Table 12.13-3 and designed to resist the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 need not comply with ACI 318 Section 18.13.3.1.

1810.3.13 Seismic Ties

Seismic ties shall comply with the provisions of ACI 318.

Exception: In Group R-3 and U occupancies of light-frame construction, deep foundation elements supporting foundation walls, isolated interior posts detailed so the element is not subject to lateral loads or exterior decks and patios are not subject to interconnection where the soils are of adequate stiffness, subject to the approval of the building official.

1810.4 Installation

Deep foundations shall be installed in accordance with Section 1810.4. Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section shall satisfy the applicable conditions of installation.

1810.4.1 Structural Integrity

Deep foundation elements shall be installed in such a manner and sequence as to prevent distortion or damage that would adversely affect the structural integrity of adjacent structures or of foundation elements being installed or already in place and as to avoid compacting the surrounding soil to the extent that other foundation elements cannot be installed properly.

1810.4.1.1 Compressive Strength of Precast Concrete Piles

A precast concrete pile shall not be driven before the concrete has attained a compressive strength of not less than 75 percent of the specified compressive strength (f 'c), but not less than the strength sufficient to withstand handling and driving forces.

1810.4.1.2 Shafts in Unstable Soils

Where cast-in-place deep foundation elements are formed through unstable soils, the open hole shall be stabilized by a casing, slurry or other approved method prior to placing the concrete. Where the casing is withdrawn during concreting, the level of concrete shall be maintained above the bottom of the casing at a sufficient height to offset any hydrostatic or lateral soil pressure. Driven casings shall be mandrel driven their full length in contact with the surrounding soil.

1810.4.1.3 Driving Near Uncased Concrete

Deep foundation elements shall not be driven within six element diameters center to center in granular soils or within one-half the element length in cohesive soils of an uncased element filled with concrete less than 48 hours old unless approved by the building official. If driving near uncased concrete elements causes the concrete surface in any completed element to rise or drop significantly or bleed additional water, the completed element shall be replaced.

1810.4.1.4 Driving Near Cased Concrete

Deep foundation elements shall not be driven within four and one-half average diameters of a cased element filled with concrete less than 24 hours old unless approved by the building official. Concrete shall not be placed in casings within heave range of driving.

1810.4.1.5 Defective Timber Piles

[OSHPD 1R, 2 & 5] Not permitted by OSHPD. Any substantial sudden change in rate of penetration of a timber pile shall be investigated for possible damage. If the sudden change in rate of penetration cannot be correlated to soil strata, the pile shall be removed for inspection or rejected.

1810.4.2 Identification

Deep foundation materials shall be identified for conformity to the specified grade with this identity maintained continuously from the point of manufacture to the point of installation or shall be tested by an approved agency to determine conformity to the specified grade. The approved agency shall furnish an affidavit of compliance to the building official.

1810.4.3 Location Plan

A plan showing the location and designation of deep foundation elements by an identification system shall be filed with the building official prior to installation of such elements. Detailed records for elements shall bear an identification corresponding to that shown on the plan.

1810.4.4 Preexcavation

The use of jetting, augering or other methods of preexcavation shall be subject to the approval of the building official. Where permitted, preexcavation shall be carried out in the same manner as used for deep foundation elements subject to load tests and in such a manner that will not impair the carrying capacity of the elements already in place or damage adjacent structures. Element tips shall be advanced below the preexcavated depth until the required resistance or penetration is obtained.

1810.4.5 Vibratory Driving

Vibratory drivers shall only be used to install deep foundation elements where the element load capacity is verified by load tests in accordance with Section 1810.3.3.1.2.

Exceptions:

- The pile installation is completed by driving with an impact hammer in accordance with Section 1810.3.3.1.1.

- The pile is to be used only for lateral resistance.

The installation of production elements shall be controlled according to power consumption, rate of penetration or other approved means that ensures element capacities equal or exceeding those of the test elements.

1810.4.6 Heaved Elements

Deep foundation elements that have heaved during the driving of adjacent elements shall be redriven as necessary to develop the required capacity and penetration, or the capacity of the element shall be verified by load tests in accordance with Section 1810.3.3.1.2.

1810.4.7 Enlarged Base Cast-in-Place Elements

Enlarged bases for cast-in-place deep foundation elements formed by compacting concrete or by driving a precast base shall be formed in or driven into granular soils. Such elements shall be constructed in the same manner as successful prototype test elements driven for the project. Shafts extending through peat or other organic soil shall be encased in a permanent steel casing. Where a cased shaft is used, the shaft shall be adequately reinforced to resist column action or the annular space around the shaft shall be filled sufficiently to reestablish lateral support by the soil. Where heave occurs, the element shall be replaced unless it is demonstrated that the element is undamaged and capable of carrying twice its design load.

1810.4.8 Hollow-Stem Augered, Cast-in-Place Elements

Where concrete or grout is placed by pumping through a hollow-stem auger, the auger shall be permitted to rotate in a clockwise direction during withdrawal. As the auger is withdrawn at a steady rate or in increments not to exceed 1 foot (305 mm), concreting or grouting pumping pressures shall be measured and maintained high enough at all times to offset hydrostatic and lateral earth pressures. Concrete or grout volumes shall be measured to ensure that the volume of concrete or grout placed in each element is equal to or greater than the theoretical volume of the hole created by the auger. Where the installation process of any element is interrupted or a loss of concreting or grouting pressure occurs, the element shall be redrilled to 5 feet (1524 mm) below the elevation of the tip of the auger when the installation was interrupted or concrete or grout pressure was lost and reformed. Augered cast-in-place elements shall not be installed within six diameters center to center of an element filled with concrete or grout less than 12 hours old, unless approved by the building official. If the concrete or grout level in any completed element drops due to installation of an adjacent element, the element shall be replaced.

1810.4.9 Socketed Drilled Shafts

The rock socket and pipe or tube casing of socketed drilled shafts shall be thoroughly cleaned of foreign materials before filling with concrete. Steel cores shall be bedded in cement grout at the base of the rock socket.

1810.4.10 Micropiles

Micropile deep foundation elements shall be permitted to be formed in holes advanced by rotary or percussive drilling methods, with or without casing. The elements shall be grouted with a fluid cement grout. The grout shall be pumped through a tremie pipe extending to the bottom of the element until grout of suitable quality returns at the top of the element. The following requirements apply to specific installation methods:

- For micropiles grouted inside a temporary casing, the reinforcing bars shall be inserted prior to withdrawal of the casing. The casing shall be withdrawn in a controlled manner with the grout level maintained at the top of the element to ensure that the grout completely fills the drill hole. During withdrawal of the casing, the grout level inside the casing shall be monitored to verify that the flow of grout inside the casing is not obstructed.

- For a micropile or portion thereof grouted in an open drill hole in soil without temporary casing, the minimum design diameter of the drill hole shall be verified by a suitable device during grouting.

- For micropiles designed for end bearing, a suitable means shall be employed to verify that the bearing surface is properly cleaned prior to grouting.

- Subsequent micropiles shall not be drilled near elements that have been grouted until the grout has had sufficient time to harden.

- Micropiles shall be grouted as soon as possible after drilling is completed.

- For micropiles designed with a full-length casing, the casing shall be pulled back to the top of the bond zone and reinserted or some other suitable means employed to ensure grout coverage outside the casing.

1810.4.11 Helical Piles

Helical piles shall be installed to specified embedment depth and torsional resistance criteria as determined by a registered design professional. The torque applied during installation shall not exceed the manufacturer's rated maximum installation torque resistance of the helical pile.

1810.4.12 Special Inspection

Special inspections in accordance with Sections 1705.7 and 1705.8 shall be provided for driven and cast-in-place deep foundation elements, respectively. Special inspections in accordance with Section 1705.9 shall be provided for helical piles.

Section 1811 Prestressed Rock and Soil Foundation Anchors [OSHPD 1R, 2 & 5]

1811.1 General

The requirements of this section address the use of vertical rock and soil anchors in resisting seismic or wind overturning forces, resulting in tension on shallow foundations.

1811.2 Adoption

Except for the modifications as set forth in Sections 1811.3 and 1811.4, all prestressed rock and soil foundation anchors shall comply with PTI Recommendations for Prestressed Rock and Soil Anchors.

1811.3 Geotechnical Requirements

The geotechnical report for the Prestressed Rock & Soil Foundation Anchors shall address the following:

- Minimum diameter and minimum spacing for the anchors including consideration of group effects.

- Maximum unbonded length and minimum bonded length of the tendon.

- Maximum recommended anchor tension capacity based upon the soil or rock strength/grout bond and anchor depth/spacing.

- Allowable bond stress at the ground/grout interface and applicable factor of safety for ultimate bond stress.

- Anchor axial tension stiffness recommendations at the anticipated anchor axial tension displacements, when required for structural analysis.

- Minimum grout pressure for installation and post-grout pressure.

- Class I corrosion protection is required for all permanent and extended temporary anchors in service more than 2 years. A minimum of Class II corrosion protection is required for temporary anchors in service less than or equal to 2 years.

- Performance test shall be at a minimum of 1.6 times the design loads, but shall not exceed 80 percent of the specified minimum tensile strength of the tendons. There shall be a minimum of two preproduction test anchors. Preproduction test anchors shall be tested to ultimate load or a maximum of 0.80 times the specified minimum tensile strength of the tendon. A creep test is required for all prestressed anchors with greater than 10 kips of lock-off prestressing load.

- Lock-off prestressing load requirements.

- Acceptable drilling methods.

- Geotechnical observation and monitoring requirements.

1811.4 Structural Requirements

- Tendons shall be thread-bar anchors conforming to ASTM A722.

- The anchors shall be placed vertical.

- Design loads shall be based upon the load combinations in Section 2.4 of ASCE 7 and shall not exceed 60 percent of the specified minimum tensile strength of the tendons.

- Ultimate load shall be based upon the lesser of the strength of the superstructure elements, the maximum forces from a fully yielded structural system and forces from the load combinations with overstrength factor in accordance with ASCE 7, Section 12.4.3 and shall not exceed 80 percent of the specified minimum tensile strength of the tendons.

- The anchor shall be designed to fail in grout bond to the soil or rock before pullout of the soil wedge by group effect.

- Foundation design shall incorporate the effect of lock-off loads.

- Design shall account for as-built locations of soil anchors considering all the acceptable construction tolerances.

- Design shall account for both short- and long-term deformation.

- Enforcement agency may require consideration of anchor deformation in evaluating deformation compatibility or building drift where it may be significant.

Section 1812 Earth Retaining Shoring [OSHPD 1R, 2 & 5]

1812.1 General

The requirements of this section shall apply to temporary and permanent earth-retaining shoring using soldier piles and lagging with or without tie-back anchors in soil or rock, only when existing or new facilities are affected. Shoring used as construction means and methods only, which does not affect existing or new facilities, is not regulated by this section and shall satisfy the requirements of the authorities having jurisdiction.

Design, construction, testing and inspection shall satisfy the requirements of this code except as modified in Sections 1812.2 through 1812.8.

1812.2 Duration

Shoring shall be considered temporary when elements of the shoring will be exposed to site conditions for a period of less than or equal to 2 years, and shall be considered permanent otherwise. Permanent shoring shall account for the increase in lateral soil pressure due to earthquake. At the end of the construction period, the existing and new structures shall not rely on the temporary shoring for support in anyway. Wood components shall not be used for permanent shoring lasting more than 2 years. Wood components of the temporary shoring that may affect the performance of permanent structure shall be removed after the shoring is no longer required.

All components of the shoring shall have corrosion protection or preservative treatment for their expected duration. Wood components of the temporary shoring that will not be removed shall be treated in accordance with AWPA U1 (Commodity Specification A, Use Category 4B and compatible species in accordance with Section 5), and shall be identified in accordance with Section 2303.1.9.

1812.3 Surcharge

Surcharge pressure due to footings, traffic or other sources shall be considered in the design. If the footing surcharge is located within the semicircular distribution or bulb of earth pressure (when shoring is located close to a footing), lagging shall be designed for lateral earth pressure due to footing surcharge. Soil arching effects may be considered in the design of lagging. Underpinning of the footing may be used in lieu of designing the shoring and lagging for surcharge pressure. Alternatively, continuously contacting drilled pier shafts near the footings shall be permitted. The lateral surcharge design pressure shall be derived using Boussinesq equations modified for the distribution of stresses in an elastic medium due to a uniform, concentrated or line surface load as appropriate and soil arching effects.

1812.4 Design and Testing

Except for the modifications as set forth in Sections 1812.4.1 through 1812.4.3, all Prestressed Rock and Soil Tie-back Anchors shall comply with PTI Recommendations for Prestressed Rock and Soil Anchors.

1812.4.1 Geotechnical Requirements

The geotechnical report for the earth retaining shoring shall address the following:

- Minimum diameter and minimum spacing for the anchors including consideration of group effects.

- Maximum unbonded length and minimum bonded length of the tie-back anchors.

- Maximum recommended anchor tension capacity based upon the soil or rock strength/grout bond and anchor depth/spacing.

- Allowable bond stress at the ground/grout interface and applicable factor of safety for ultimate bond stress for the anchor. For permanent anchors, a minimum factor of safety of 2.0 shall be applied to the ground soil interface as required by PTI Recommendations for Prestressed Rock and Soil Anchors Section 6.6.

- Minimum grout pressure for installation and post-grout pressure for the anchor. The presumptive post-grout pressure of 300 psi may be used for all soil types.

- Class I corrosion protection is required for all permanent and extended temporary anchors in service more than 2 years. A minimum of Class II corrosion protection is required for temporary anchors in service less than or equal to 2 years.

- Performance test for the anchors shall be at a minimum of two times the design loads and shall not exceed 80 percent of the specified minimum tensile strength of the anchor rod. A creep test is required for all prestressed anchors that are performance tested. All production anchors shall be tested at 150 percent of design loads and shall not be greater than 70 percent of the specified minimum tensile strength of the anchor rod.

- Earth pressure, surcharge pressure and the seismic increment of earth pressure loading, when applicable.

- Maximum recommended lateral deformation at the top of the soldier pile, at the tie-back anchor locations and the drilled pier concrete shafts at the lowest grade level.

- Allowable vertical soil bearing pressure, friction resistance and lateral passive soil resistance for the drilled pier concrete shafts and associated factors of safety for these allowable capacities.

- Soil-pier shaft/pile interaction assumptions and lateral soil stiffness to be used in design for drilled pier concrete shaft or pile lateral loads.

- Acceptable drilling methods.

- Geotechnical observation and monitoring recommendations.

1812.4.2 Structural Requirements:

- Tendons shall be thread-bar anchors conforming to ASTM A722.

- Anchor design loads shall be based upon the load combinations in Section 2.4 of ASCE 7 and shall not exceed 60 percent of the specified minimum tensile strength of the tendons.

- The anchor shall be designed to fail in grout bond to the soil or rock before pullout of the soil wedge.

- Design of shoring system shall account for as-built locations of soil anchors considering all specified construction tolerances in Section 1812.8

- Design of shoring system shall account for both short- and long-term deformation.

1812.4.3 Testing of Tie-Back Anchors:

- The geotechnical engineer shall keep a record at the job site of all test loads and total anchor movement and report their accuracy.

- If a tie-back anchor initially fails the testing requirements, the anchor shall be permitted to be re-grouted and retested. If the anchor continues to fail, the followings steps shall be taken:

  - The contractor shall determine the cause of failure: (variations of the soil conditions, installation methods, materials, etc.).

  - The contractor shall propose a solution to remedy the problem. The proposed solution will need to be reviewed and approved by geotechnical engineer, shoring design engineer and the building official.

- After a satisfactory test, each anchor shall be locked off in accordance with PTI Recommendations for Prestressed Rock and Soil Anchors Section 8.4.

- The shoring design engineer shall specify design loads for each anchor.

1812.5 Construction

The construction procedure shall address the following:

- Holes drilled for piles/tie-back anchors shall be done without detrimental loss of ground, sloughing or caving of materials and without endangering previously installed shoring members or existing foundations.

- Drilling of earth anchor shafts for tie-backs shall occur when the drill bench reaches 2 to 3 feet below the level of the tie-back pockets.

- Casing or other methods shall be used where necessary to prevent loss of ground and collapse of the hole.

- Drill cuttings from the earth anchor shaft shall be removed prior to anchor installation.

- Unless tremie methods are used, all water and loose materials shall be removed from the holes prior to installing piles/tie-backs.

- Tie-back anchor rods with attached centralizing devices shall be installed into the shaft or through the drill casing. Centralizing devices shall not restrict movement of the grout.

- After lagging installation, voids between lagging and soil shall be backfilled immediately to the full height of lagging.

- The soldier piles shall be placed within specified tolerances in the drilled hole and braced against displacement during grouting. Shafts shall be filled with concrete up to the elevation shown on the construction documents. The remainder of the shaft shall be permitted to be filled with controlled low-strength material (CLSM), when permitted by the construction documents. Excavation for lagging shall not be started until concrete has achieved sufficient strength for all anticipated loads as determined by the shoring design engineer.

- Where boulders and/or cobbles have been identified in the geotechnical reports, the contractor shall be prepared to address boulders and/or cobbles that may be encountered during the drilling of soldier piles and tie-back anchors.

- The grouting equipment shall produce grout free of lumps and indispensed cement. The grouting equipment shall be sized to enable the grout to be pumped in continuous operation. The mixer shall be capable of continuously agitating the grout.

- The quantity of grout and grout pressure shall be recorded. The grout pressure shall be controlled to prevent excessive heave in soils or fracturing rock formations.

- If post-grouting is required, post-grouting operation shall be performed after initial grout has set for 24 hours in the bond length only. Tie-backs shall be grouted over a sufficient length (anchor bond length) to transfer the maximum anchor force to the anchor grout.

- Testing of anchors may be performed after post-grouting operations, provided that grout has reached a strength of 3,000 psi as required by PTI Recommendations for Prestressed Rock and Soil Anchors Section 6.11.

- Anchor rods shall be tensioned straight and true. Excavation directly below the anchors shall not continue before those anchors are tested.

1812.6 Inspection, Survey Monitoring and Observation

- The shoring design engineer or his designee shall make periodic inspections of the job site for the purpose of observing the installation of the shoring system, testing of tie-back anchors and monitoring of the survey.

- Testing, inspection and observation shall be in accordance with testing, inspection and observation requirements approved by the building official. The following activities and materials shall be tested, inspected or observed by the special inspector and geotechnical engineer:

  - Sampling and testing of concrete in soldier pile and tie-back anchor shafts.

  - Fabrication of tie-back anchor pockets on soldier beams

  - Installation and testing of tie-back anchors.

  - Survey monitoring of soldier pile and tie-back load cells.

  - Survey monitoring of existing buildings.

- A complete and accurate record of all soldier pile locations, depths, concrete strengths, tie-back locations and lengths, tie-back grout strength, quantity of concrete per pile, quantity of grout per tie-back and applied tie-back loads shall be maintained by the special inspector and geotechnical engineer. The shoring design engineer shall be notified of any unusual conditions encountered during installation.

- Calibration data for each test jack, pressure gauge and master pressure gauge shall be verified by the special inspector and geotechnical engineer. The calibration tests shall be performed by an independent testing laboratory and within 120 calendar days of the data submitted.

- Monitoring points shall be established at the top and at the anchor heads of selected soldier piles and at intermediate intervals as considered appropriate by the geotechnical engineer.

- Control points shall be established outside the area of influence of the shoring system to ensure the accuracy of the monitoring readings.

- The periodic basis of shoring monitoring, at a minimum, shall be as follows:

  - Initial monitoring shall be performed prior to any excavation.

  - Once excavation has begun, the periodic readings shall be taken weekly until excavation reaches the estimated subgrade elevation and the permanent foundation is complete.

  - If performance of the shoring is within established guidelines, shoring design engineer may permit the periodic readings to be biweekly. Once initiated, biweekly readings shall continue until the building slab at ground floor level is completed and capable of transmitting lateral loads to the permanent structure. Thereafter, readings can be monthly.

  - Where the building has been designed to resist lateral earth pressures, the periodic monitoring of the soldier piles and adjacent structure can be discontinued once the ground floor diaphragm and subterranean portion of the structure is capable of resisting lateral soil loads and approved by the shoring design engineer, geotechnical engineer and the building official.

  - Additional readings shall be taken when requested by special inspector, shoring design engineer, geotechnical engineer or the building official.

- Monitoring readings shall be submitted to shoring design engineer, engineer in responsible charge, and the building official within 3 working days after they are conducted. Monitoring readings shall be accurate to within 0.01 feet. Results are to be submitted in tabular form showing at least the initial date of monitoring and reading, current monitoring date and reading and difference between the two readings.

- If the total cumulative horizontal or vertical movement (from start of construction) of the existing buildings reaches 1/2 inch or soldier piles movement reaches 1 inch all excavation activities shall be suspended. The geotechnical and shoring design engineers shall determine the cause of movement, if any, and recommend corrective measures, if necessary, before excavation continues.

- If the total cumulative horizontal or vertical movement (from start of construction) of the existing buildings reaches 3/4 inch or soldier piles movement reaches 11/2 inches all excavation activities shall be suspended until the causes, if any, can be determined. Supplemental shoring shall be devised to eliminate further movement and the building official shall review and approve the supplemental shoring before excavation continues.

- Monitoring of tie-back anchor loads:

  - Load cells shall be installed at the tie-back heads adjacent to buildings at maximum interval of 50 feet, with a minimum of one load cell per wall.

  - Load cell readings shall be taken once a day during excavation and once a week during the remainder of construction.

  - Load cell readings shall be submitted to the geotechnical engineer, shoring design engineer, engineer in responsible charge and the building official.

  - Load cell readings can be terminated once the temporary shoring no longer provides support for the buildings.

1812.7 Monitoring of Existing OSHPD 1, 1R, 2, 4 and 5 Structures

- The contractor shall complete a written and photographic log of all existing OSHPD 1, 1R, 2, 4 & 5 structures within 100 feet or three times depth of shoring, prior to construction. A licensed surveyor shall document all existing substantial cracks in adjacent existing structures.

- The contractor shall document the existing condition of wall cracks adjacent to shoring walls prior to start of construction.

- The contractor shall monitor existing walls for movement or cracking that may result from adjacent shoring.

- If excessive movement or visible cracking occurs, the contractor shall stop work and shore/reinforce excavation and contact the shoring design engineer and the building official.

- Monitoring of the existing structure shall be at reasonable intervals as required by the registered design professional, subject to approval of the building official. Monitoring shall be performed by a licensed surveyor and shall consist of vertical and lateral movement of the existing structures. Prior to starting shoring installation a preconstruction meeting shall take place between the contractor, shoring design engineer, surveyor, geotechnical engineer and the building official to identify monitoring locations on existing buildings.

- If in the opinion of the building official or shoring design engineer, monitoring data indicate excessive movement or other distress, all excavation shall cease until the geotechnical engineer and shoring design engineer investigate the situation and make recommendations for remediation or continuing.

- All reading and measurements shall be submitted to the building official and shoring design engineer.

1812.8 Tolerances

The following tolerances shall be specified on the construction documents.

- Soldier piles:

  - Horizontal and vertical construction tolerances for the soldier pile locations.

  - Soldier pile plumbness requirements (angle with vertical line).

- Tie-back anchors:

  - Allowable deviation of anchor projected angle from specified vertical and horizontal design projected angle.

  - Anchor clearance to the existing/new utilities and structures.

Section 1813 Vibro Stone Columns for Ground Improvement [OSHPD 1R, 2 & 5]

1813.1 General

This section shall apply to Vibro Stone Columns (VSCs) for ground improvement using unbounded aggregate materials. Vibro stone column provisions in this section are intended to increase bearing capacity, reduce settlements and mitigate liquefaction for shallow foundations. These requirements shall not be used for grouted or bonded stone columns, ground improvement for deep foundation elements or changing site class. VSCs shall not be considered as a deep foundation element.

Ground improvement shall be installed under the entire building/structure footprint and not under isolated foundation elements only.

Design, construction, testing and inspection shall satisfy the requirements of this code except as modified in Sections 1813.2 through 1813.5.

1813.2 Geotechnical Report

The geotechnical report shall specify vibro stone column requirements to ensure uniformity in total and differential immediate settlement, long-term settlement and earthquake-induced settlement. The report shall address the following:

- Soil compaction shall be sufficient to mitigate potential for liquefaction as described in California Geological Survey (CGS) Special Publication 117A (SP-117A): Guidelines for Evaluating and Mitigating Seismic Hazard in California.

- The area replacement ratio for the compaction elements and the basis of its determination shall be explained. Minimum factor of safety for soil compaction shall be in accordance with SP-117A.

- The depth of soil compaction elements and extent beyond the footprint of structures/foundation shall be defined. Extent beyond the foundation shall be half the depth of the VSCs with a minimum of 10' or an approved alternative.

- The minimum diameter and maximum spacing of soil compaction elements shall be specified. VSCs shall not be less than 2 feet in diameter and center to center spacing shall not exceed 8 feet.

- The modulus of subgrade reactions for shallow foundations shall account for the presence of compaction elements.

- The modulus of subgrade reactions, long-term settlement and post-earthquake settlement shall be specified along with expected total and differential settlements for design.

- The acceptance criteria for friction cone and piezocone penetration testing in accordance with ASTM D5778 complemented by a standard penetration test (SPT) in accordance with ASTM D1586, if necessary, to verify soil improvement shall be specified

- The requirements for special inspection and observation by the geotechnical engineer shall be specified.

- A Final Verified Report (FVR) documenting the installation of the ground improvement system and confirming that the ground improvement acceptance criteria have been met shall be prepared by the geotechnical engineer and submitted to the enforcement agency for review and approval.

1813.3 Shallow Foundations

VSCs under the shallow foundation shall be located symmetrically around the centroid of the footing or load, and:

- There shall be a minimum of four stone columns under each isolated or continuous/combined footing or an approved equivalent.

- The VSCs or deep foundation elements shall not be used to resist tension or overturning uplift from the shallow foundations.

- The foundation design for the shallow foundation shall consider the increased vertical stiffness of the VSCs as point supports for analysis, unless it is substantiated that the installation of the VSCs results in improvement of the surrounding soils such that the modulus of subgrade reaction, long-term settlement and post-earthquake settlement can be considered uniform throughout.

1813.4 Installation

VSCs shall be installed with vibratory probes. Vertical columns of compacted unbounded aggregate shall be formed through the soils to be improved by adding gravel near the tip of the vibrator and progressively raising and re-penetrating the vibrator, which will results in the gravel being pushed into the surrounding soil.

Gravel aggregate for VSCs shall be well graded with a maximum size of 6 inches and not more than 10 percent smaller than 3/8 inch after compaction.

1813.5 Construction Documents

Construction documents for VSCs, at a minimum, shall include the following:

- Size, depth and location of VSCs.

- The extent of soil improvements along with building/structure foundation outlines.

- Field verification requirements and acceptance criteria using CPT/SPT.

- The locations where CPT/SPT shall be performed.

- A Testing, Inspection and Observation (TIO) program indicating the inspection and observation required for the VSCs.