Chapter 18A Soils and Foundations

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE
CHAPTER 18A — SOILS AND FOUNDATIONS

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC-CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter |  |  |  |  |  |  |  | X | X | X |  |  |  | X |  |  |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 18A provides criteria for geotechnical and structural considerations in the selection, design and installation of foundation systems to support the loads from the structure above. Chapter 18A is applicable to structures regulated by the Division of the State Architect-Structural Safety—including public elementary and secondary schools, community colleges, and state-owned or stateleased essential services buildings (applications listed in Sections 1.9.2.1 [DSA-SS] and 1.9.2.2 [DSA-SS/CC])—and by the Department of Health Care Access and Information/Office of Statewide Hospital Planning and Development—including hospitals and correctional treatment centers (applications listed in Sections 1.10.1 [OSHPD 1] and 1.10.4 [OSHPD 4]).

Section 1801A General

1801A.1 Scope

The provisions of this chapter shall apply to building and foundation systems.

1801A.1.1 Application

The scope of application of Chapter 18A is as follows:

- Structures regulated by the Division of the State Architect—Structural Safety, which include those applications listed in Section 1.9.2.1 (DSA-SS) and 1.9.2.2 (DSA-SS/CC). These applications include public elementary and secondary schools, community colleges and state-owned or state-leased essential services buildings

- Applications listed in Section 1.10.1 and 1.10.4 regulated by the Department of Health Care Access and Information/Office of Statewide Hospital Planning and Development (OSHPD).These applications include hospitals and correctional treatment centers.

1801A.1.2 Amendments in This Chapter

OSHPD adopt this chapter and all amendments.

Exception: Amendments adopted by only one agency appear in this chapter preceded with the appropriate acronym of the adopting agency, as follows:

- Division of the State Architect-Structural Safety:

  - [DSA-SS] For applications listed in Section 1.9.2.1.

  - [DSA-SS/CC] For applications listed in Section 1.9.2.2.

- Office of Statewide Hospital Planning and Development:

  - [OSHPD 1] - For applications listed in Section 1.10.1.

  - [OSHPD 4] - For applications listed in Section 1.10.4.

1801A.1.3 Reference to Other Chapters

1801A.1.3.1 [DSA-SS/CC]

Where reference within this chapter is made to sections in Chapters 16A, 19A, 21A and 22A, the provisions in Chapters 16, 19, 21 and 22, respectively shall apply instead as defined in Section 1.9.2.2. Referenced sections may not directly correlate, but the corresponding DSA-SS/CC sections to such references still apply.

Section 1802A Design Basis

1802A.1 General

Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605A.2. The quality and design of materials used structurally in excavations and foundations shall comply with the requirements specified in Chapters 16, 19, 21, 22 and 23. Excavations and fills shall comply with Chapter 33.

Section 1803A Geotechnical Investigations

1803A.1 General

Geotechnical investigations shall be conducted in accordance with Section 1803A.2 and reported in accordance with Section 1803A.7. The classification and investigation of the soil shall be made under the responsible charge of a California registered geotechnical engineer. All recommendations contained in geotechnical and geohazard reports shall be subject to the approval of the enforcement agency. All reports shall be prepared and signed by a registered geotechnical engineer, a certified engineering geologist and a registered geophysicist, where applicable.

1803A.2 Investigations Required

Geotechnical investigations shall be conducted in accordance with Sections 1803A.3 through 1803A.6.

Exceptions:

- Geotechnical reports are not required for one-story, wood-frame and light-steel-frame buildings of Type II or Type V construction and 4,000 square feet (371 m2) or less in floor area, not located within Earthquake Fault Zones or Seismic Hazard Zones as shown in the most recently published maps from the California Geological Survey (CGS) or in seismic hazard zones as defined in the Safety Element of the local General Plan. Allowable foundation and lateral soil pressure values may be determined from Table 1806A.2.

- A previous report for a specific site may be resubmitted, provided that a reevaluation is made and the report is found to be currently appropriate.

1803A.3 Basis of Investigation

Soil classification shall be based on observation and any necessary tests of the materials disclosed by borings, test pits or other subsurface exploration made in appropriate locations. Additional studies shall be made as necessary to evaluate slope stability, soil strength, position and adequacy of load-bearing soils, the effect of moisture variation on soil-bearing capacity, compressibility, liquefaction and expansiveness.

1803A.3.1 Scope of Investigation

The scope of the geotechnical investigation including the number and types of borings or soundings, the equipment used to drill or sample, the in-situ testing equipment and the laboratory testing program shall be determined by a registered design professional.

There shall not be less than one boring or exploration shaft for each 5,000 square feet (465 m2) of building area at the foundation level with a minimum of two provided for any one building. A boring may be considered to reflect subsurface conditions relevant to more than one building, subject to the approval of the enforcement agency.

Borings shall be of sufficient size to permit visual examination of the soil in place or, in lieu thereof, cores shall be taken.

Borings shall be of sufficient depth and size to adequately characterize sub-surface conditions.

1803A.4 Qualified Representative

The investigation procedure and apparatus shall be in accordance with generally accepted engineering practice. The registered design professional shall have a fully qualified representative on site during all boring or sampling operations.

1803A.5 Investigated Conditions

Geotechnical investigations shall be conducted as indicated in Sections 1803A.5.1 through 1803A.5.12.

1803A.5.1 Classification

Soil materials shall be classified in accordance with ASTM D2487. Rock shall be classified in accordancewith ASTM D5878.

1803A.5.2 Questionable Soil and Rock

Where the classification, strength, moisture sensitivity or compressibility of the soil or rock is in doubt or where a load-bearing value superior to that specified in this code is claimed, the building official shall be permitted to require that a geotechnical investigation be conducted.

1803A.5.3 Expansive Soil

In areas likely to have expansive soil, the building official shall require soil tests to determine where such soils do exist.

Soils meeting all four of the following provisions shall be considered to be expansive, except that tests to show compliance with Items 1, 2 and 3 shall not be required if the test prescribed in Item 4 is conducted:

- Plasticity index (PI) of 15 or greater, determined in accordance with ASTM D4318.

- More than 10 percent of the soil particles pass a No.200 sieve (75 µm), determined in accordance with ASTM D6913.

- More than 10 percent of the soil particles are less than 5 micrometers in size, determined in accordance with ASTM D6913.

- Expansion index greater than 20, determined in accordance with ASTM D4829.

1803A.5.4 Groundwater

A geotechnical investigation shall be performed to determine if:

- Groundwater is above or within 5 feet (1524 mm) below the elevation of the lowest floor level where such floor is located below the finished ground level adjacent to the foundation.

- The groundwater depth will affect the design and construction of buildings and structures.

1803A.5.5 Deep Foundations

Where deep foundations will be used, a geotechnical investigation shall be conducted and shall include all of the following, unless sufficient data on which to base the design and installation is otherwise available:

- Recommended deep foundation types and installed capacities.

- Recommended center-to-center spacing of deep foundation elements.

- Driving criteria.

- Installation procedures.

- Field inspection and reporting procedures (to include procedures for verification of the installed bearing capacity where required).

- Load test requirements.

- Suitability of deep foundation materials for the intended environment.

- Designation of bearing stratum or strata.

- Reductions for group action, where necessary.

1803A.5.6 Rock Strata

Where foundations are to be constructed on or in rock, the geotechnical investigation shall assess variations in rock strata depth, competency and load-bearing capacity.

1803A.5.7 Excavation Near Foundations

Where excavation will reduce support from any foundation, a registered design professional shall prepare an assessment of the structure as determined from examination of the structure, available design documents, available subsurface data, and, if necessary, excavation of test pits. The registered design professional shall determine the requirements for support and protection of any existing foundation and prepare site-specific plans, details and sequence of work for submission. Such support shall be provided by under-pinning, bracing, excavation retention systems or by other means acceptable to the building official.

1803A.5.8 Compacted Fill Material

Where shallow foundations will bear on compacted fill material more than 12 inches (305 mm) in depth, a geotechnical investigation shall be conducted and shall include all of the following:

- Specifications for the preparation of the site prior to placement of compacted fill material.

- Specifications for material to be used as compacted fill.

- Test methods to be used to determine the maximum dry density and optimum moisture content of the material to be used as compacted fill.

- Maximum allowable thickness of each lift of compacted fill material.

- Field test method for determining the in-place dry density of the compacted fill.

- Minimum acceptable in-place dry density expressed as a percentage of the maximum dry density determined in accordance with Item 3.

- Number and frequency of field tests required to determine compliance with Item 6.

1803A.5.9 Controlled Low-Strength Material (CLSM)

Where shallow foundations will bear on controlled low-strength material (CLSM), a geotechnical investigation shall be conducted and shall include all of the following:

- Specifications for the preparation of the site prior to placement of the CLSM.

- Specifications for the CLSM.

- Laboratory or field test method(s) to be used to determine the compressive strength or bearing capacity of the CLSM.

- Test methods for determining the acceptance of the CLSM in the field.

- Number and frequency of field tests required to determine compliance with Item 4.

1803A.5.10 Alternate Setback and Clearance

Where setbacks or clearances other than those required in Section 1808A.7 are desired, the building official shall be permitted to require a geotechnical investigation by a registered design professional to demonstrate that the intent of Section 1808A.7 would be satisfied. Such an investigation shall include consideration of material, height of slope, slope gradient, load intensity and erosion characteristics of slope material.

1803A.5.11 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F, a geotechnical investigation shall be conducted, and shall include an evaluation of all of the following potential geologic and seismic hazards:

- Slope instability.

- Liquefaction.

- Total and differential settlement.

- Surface displacement due to faulting or seismically induced lateral spreading or lateral flow.

1803A.5.12 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, the geotechnical investigation required by Section 1803A.5.11 shall include all of the following as applicable:

- The determination of dynamic seismic lateral earth pressures on foundation walls and retaining walls supporting more than 6 feet (1.83 m) of backfill height due to design earthquake ground motions.

- The potential for liquefaction and soil strength loss evaluated for site peak ground acceleration, earthquake magnitude and source characteristics consistent with the maximum considered earthquake ground motions. Peak ground acceleration shall be determined based on one of the following:

  - A site-specific study in accordance with Chapter 21 of ASCE 7.

  - In accordance with Section 11.8.3 of ASCE 7.

- An assessment of potential consequences of liquefaction and soil strength loss including, but not limited to, the following:

  - Estimation of total and differential settlement.

  - Lateral soil movement.

  - Lateral soil loads on foundations.

  - Reduction in foundation soil-bearing capacity and lateral soil reaction.

  - Soil downdrag and reduction in axial and lateral soil reaction for pile foundations.

  - Increases in soil lateral pressures on retaining walls.

  - Flotation of buried structures.

- Discussion of mitigation measures such as, but not limited to, the following:

  - Selection of appropriate foundation type and depths.

  - Selection of appropriate structural systems to accommodate anticipated displacements and forces.

  - Ground stabilization.

  - Any combination of these measures and how they shall be considered in the design of the structure.

1803A.6 Geohazard Reports

Geohazard reports shall be required for all proposed construction.

Exceptions:

- Reports are not required for one-story, wood-frame and light-steel-frame buildings of Type II or Type V construction and 4,000 square feet (371 m2) or less in floor area, not located within Earthquake Fault Zones or Seismic Hazard Zones as shown in the most recently published maps from the California Geological Survey (CGS) or in seismic hazard zones as defined in the Safety Element of the local General Plan.

- Reports are not required for the following scopes of work in existing buildings: nonstructural alterations, voluntary structural alterations without foundation work, or structural repairs for damage not caused by an earthquake. [OSHPD 1 & 4] Incidental structural additions or alterations.

- A previous report for a specific site may be resubmitted, provided that a reevaluation is made and the report is found to be currently appropriate.

The purpose of the geohazard report shall be to identify geologic and seismic conditions that may require project mitigations. The reports shall contain data which provide an assessment of the nature of the site and potential for earthquake damage based on appropriate investigations of the regional and site geology, project foundation conditions and the potential seismic shaking at the site. The report shall be prepared by a California-certified engineering geologist in consultation with a California-registered geotechnical engineer.

The preparation of the geohazard report shall consider the most recent CGS Note 48; Checklist for the Review of Engineering Geology and Seismology Reports for California Public School, Hospitals and Essential Services Buildings. In addition, the most recent version of CGS Special Publication 42: Earthquake Fault Zones, A Guide for Government Agencies, Property Owners / Developers, and Geoscience Practitioners for Assessing Fault Rupture Hazards in California, shall be considered for project sites proposed within an Alquist-Priolo Earthquake Fault Zone. The most recent version of CGS Special Publication 117, Guidelines for Evaluating and Mitigating Seismic Hazards in California, shall be considered for project sites proposed within a Seismic Hazard Zone. All conclusions shall be fully supported by satisfactory data and analysis.

In addition to requirements in Sections 1803A.5.11 and 1803A.5.12, the report shall include, but need not be limited to, the following:

- Site geology.

- Evaluation of the known active and potentially active faults, both regional and local.

- Ground-motion parameters, as required by Sections 1613A and 1617A, and ASCE 7.

1803A.7 Geotechnical Reporting

Where geotechnical investigations are required, a written report of the investigations shall be submitted to the building official by the permit applicant at the time of permit application. The geotechnical report shall provide completed evaluations of the foundation conditions of the site and the potential geologic/seismic hazards affecting the site. The geotechnical report shall include, but shall not be limited to, site-specific evaluations of design criteria related to the nature and extent of foundation materials, groundwater conditions, liquefaction potential, settlement potential and slope stability. The report shall contain the results of the analyses of problem areas identified in the geohazard report. The geotechnical report shall incorporate estimates of the characteristics of site ground motion provided in the geohazard report. This geotechnical report shall include, but need not be limited to, the following information:

- A plot showing the location of the soil investigations.

- A complete record of the soil boring and penetration test logs and soil samples.

- A record of the soil profile.

- Elevation of the water table, if encountered. Historic high ground water elevations shall be addressed in the report to adequately evaluate liquefaction and settlement potential.

- Recommendations for foundation type and design criteria, including but not limited to: bearing capacity of natural or compacted soil; provisions to mitigate the effects of expansive soils; mitigation of the effects of liquefaction, differential settlement and varying soil strength; and the effects of adjacent loads.

- Expected total and differential settlement.

- Deep foundation information in accordance with Section 1803A.5.5.

- Special design and construction provisions for foundations of structures founded on expansive soils, as necessary.

- Compacted fill material properties and testing in accordance with Section 1803A.5.8.

- Controlled low-strength material properties and testing in accordance with Section 1803A.5.9.

- The report shall consider the effects of stepped footings addressed in Section 1809A.3.

- The report shall consider the effects of seismic hazards in accordance with Section 1803A.6 and shall incorporate the associated geohazard report.

1803A.8 Geotechnical Peer Review

[DSA-SS and DSA-SS/CC] When alternate foundations designs or ground improvements are employed or where slope stabilization is required, a qualified peer review by a California-licensed geotechnical engineer, in accordance with Section 322 of Part 10, Title 24, CCR, may be required by the enforcement agency. In Section 322 of Part 10, Title 24, CCR, where reference is made to structural or seismic-resisting system, it shall be replaced with geotechnical, foundation or ground improvement, as appropriate.

Section 1804A Excavation, Grading and Fill

1804A.1 Excavation Near Foundations

Excavation for any purpose shall not reduce vertical or lateral support for any foundation or adjacent foundation without first underpinning or protecting the foundation against detrimental lateral or vertical movement, or both, in accordance with Section 1803A.5.7.

1804A.2 Underpinning

Where underpinning is chosen to provide the protection or support of adjacent structures, the underpinning system shall be designed and installed in accordance with provisions of this chapter and Chapter 33.

1804A.2.1 Underpinning Sequencing

Underpinning shall be installed in a sequential manner that protects the neighboring structure and the working construction site. The sequence of installation shall be identified in the approved construction documents.

1804A.3 Placement of Backfill

The excavation outside the foundation shall be backfilled with soil that is free of organic material, construction debris, cobbles and boulders or with a controlled low-strength material (CLSM). The backfill shall be placed in lifts and compacted in a manner that does not damage the foundation or the waterproofing or dampproofing material.

Exception: CLSM need not be compacted.

1804A.4 Site Grading

The ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than 1 unit vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. If physical obstructions or lot lines prohibit 10 feet (3048 mm) of horizontal distance, a 5-percent slope shall be provided to an approved alternative method of diverting water away from the foundation. Swales used for this purpose shall be sloped not less than 2 percent where located within 10 feet (3048 mm) of the building foundation. Impervious surfaces within 10 feet (3048 mm) of the building foundation shall be sloped not less than 2 percent away from the building.

Exceptions:

- Where climatic or soil conditions warrant, the slope of the ground away from the building foundation shall be permitted to be reduced to not less than 1 unit vertical in 48 units horizontal (2-percent slope).

- Impervious surfaces shall be permitted to be sloped less than 2 percent where the surface is a door landing or ramp that is required to comply with Section 1010.1.4, 1012.3 or 1012.6.1.

The procedure used to establish the final ground level adjacent to the foundation shall account for additional settlement of the backfill.

1804A.5 Grading and Fill in Flood Hazard Areas

In flood hazard areas established in Section 1612A.3, grading, fill, or both, shall not be approved:

- Unless such fill is placed, compacted and sloped to minimize shifting, slumping and erosion during the rise and fall of flood water and, as applicable, wave action.

- In floodways, unless it has been demonstrated through hydrologic and hydraulic analyses performed by a registered design professional in accordance with standard engineering practice that the proposed grading or fill, or both, will not result in any increase in flood levels during the occurrence of the design flood.

- In coastal high hazard areas, unless such fill is conducted or placed to avoid diversion of water and waves toward any building or structure.

- Where design flood elevations are specified but floodways have not been designated, unless it has been demonstrated that the cumulative effect of the proposed flood hazard area encroachment, when combined with all other existing and anticipated flood hazard area encroachment, will not increase the design flood elevation more than 1 foot (305 mm) at any point.

1804A.6 Compacted Fill Material

Where shallow foundations will bear on compacted fill material, the compacted fill shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803A.

Exception: Compacted fill material 12 inches (305 mm) in depth or less need not comply with an approved report, provided that the in-place dry density is not less than 90 percent of the maximum dry density at optimum moisture content determined in accordance with ASTM D1557. The compaction shall be verified by special inspection in accordance with Section 1705A.6.

1804A.7 Controlled Low-Strength Material (CLSM)

Where shallow foundations will bear on controlled low-strength material (CLSM), the CLSM shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803A.

Section 1805A Dampproofing and Waterproofing

1805A.1 General

Walls or portions thereof that retain earth and enclose interior spaces and floors below grade shall be waterproofed and dampproofed in accordance with this section, with the exception of those spaces containing groups other than residential and institutional where such omission is not detrimental to the building or occupancy.

Ventilation for crawl spaces shall comply with Section 1202.4.

1805A.1.1 Story Above Grade Plane

Where a basement is considered a story above grade plane and the finished ground level adjacent to the basement wall is below the basement floor elevation for 25 percent or more of the perimeter, the floor and walls shall be dampproofed in accordance with Section 1805A.2 and a foundation drain shall be installed in accordance with Section 1805A.4.2. The foundation drain shall be installed around the portion of the perimeter where the basement floor is below ground level. The provisions of Sections 1803A.5.4, 1805A.3 and 1805A.4.1 shall not apply in this case.

1805A.1.2 Under-Floor Space

The finished ground level of an under-floor space such as a crawl space shall not be located below the bottom of the footings. Where there is evidence that the ground-water table rises to within 6 inches (152 mm) of the ground level at the outside building perimeter, or that the surface water does not readily drain from the building site, the ground level of the under-floor space shall be as high as the outside finished ground level, unless an approved drainage system is provided. The provisions of Sections 1803A.5.4, 1805A.2, 1805A.3 and 1805A.4 shall not apply in this case.

1805A.1.2.1 Flood Hazard Areas

For buildings and structures in flood hazard areas as established in Section 1612A.3, the finished ground level of an under-floor space such as a crawl space shall be equal to or higher than the outside finished ground level on one side or more.

Exception: Under-floor spaces of Group R-3 buildings that meet the requirements of FEMA TB 11.

1805A.1.3 Ground-Water Control

Where the ground-water table is lowered and maintained at an elevation not less than 6 inches (152 mm) below the bottom of the lowest floor, the floor and walls shall be dampproofed in accordance with Section 1805A.2. The design of the system to lower the ground-water table shall be based on accepted principles of engineering that shall consider, but not necessarily be limited to, permeability of the soil, rate at which water enters the drainage system, rated capacity of pumps, head against which pumps are to operate and the rated capacity of the disposal area of the system.

1805A.2 Dampproofing

Where hydrostatic pressure will not occur as determined by Section 1803A.5.4, floors and walls shall be dampproofed in accordance with this section.

1805A.2.1 Floors

Dampproofing materials for floors shall be installed between the floor and the base course required by Section 1805A.4.1, except where a separate floor is provided above a concrete slab.

Where installed beneath the slab, dampproofing shall consist of not less than 6-mil (0.006 inch; 0.152 mm) polyethylene with joints lapped not less than 6 inches (152 mm), or other approved methods or materials. Where permitted to be installed on top of the slab, dampproofing shall consist of mopped-on bitumen, not less than 4-mil (0.004 inch; 0.102 mm) polyethylene, or other approved methods or materials. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

1805A.2.2 Walls

Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level.

Dampproofing shall consist of a bituminous material, 3 pounds per square yard (16 N/m2) of acrylic modified cement, 1/8 inch (3.2 mm) coat of surface-bonding mortar complying with ASTM C887, any of the materials permitted for waterproofing by Section 1805.3.2 or other approved methods or materials.

1805A.2.2.1 Surface Preparation of Walls

Prior to application of dampproofing materials on concrete walls, holes and recesses resulting from the removal of form ties shall be sealed with a bituminous material or other approved methods or materials. Unit masonry walls shall be parged on the exterior surface below ground level with not less than 3/8 inch (9.5 mm) of Portland cement mortar. The parging shall be coved at the footing.

Exception: Parging of unit masonry walls is not required where a material is approved for direct application to the masonry.

1805A.3 Waterproofing

Where the ground-water investigation required by Section 1803A.5.4 indicates that a hydrostatic pressure condition exists, and the design does not include a ground-water control system as described in Section 1805A.1.3, walls and floors shall be waterproofed in accordance with this section.

1805A.3.1 Floors

Floors required to be waterproofed shall be of concrete and designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected.

Waterproofing shall be accomplished by placing a membrane of rubberized asphalt, butyl rubber, fully adhered/fully bonded HDPE or polyolefin composite membrane or not less than 6-mil [0.006 inch (0.152 mm)] polyvinyl chloride with joints lapped not less than 6 inches (152 mm) or other approved materials under the slab. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

1805A.3.2 Walls

Walls required to be waterproofed shall be of concrete or masonry and shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected.

Waterproofing shall be applied from the bottom of the wall to not less than 12 inches (305 mm) above the maximum elevation of the ground-water table. The remainder of the wall shall be dampproofed in accordance with Section 1805A.2.2. Waterproofing shall consist of two-ply hot-mopped felts, not less than 6-mil (0.006 inch; 0.152 mm) polyvinyl chloride, 40-mil (0.040 inch; 1.02 mm) polymer-modified asphalt, 6-mil (0.006 inch; 0.152 mm) polyethylene or other approved methods or materials capable of bridging nonstructural cracks. Joints in the membrane shall be lapped and sealed in accordance with the manufacturer's installation instructions.

1805A.3.2.1 Surface Preparation of Walls

Prior to the application of waterproofing materials on concrete or masonry walls, the walls shall be prepared in accordance with Section 1805A.2.2.1.

1805A.3.3 Joints and Penetrations

Joints in walls and floors, joints between the wall and floor and penetrations of the wall and floor shall be made watertight utilizing approved methods and materials.

1805A.4 Subsoil Drainage System

Where a hydrostatic pressure condition does not exist, dampproofing shall be provided and a base shall be installed under the floor and a drain installed around the foundation perimeter. A subsoil drainage system designed and constructed in accordance with Section 1805A.1.3 shall be deemed adequate for lowering the ground-water table.

1805A.4.1 Floor Base Course

Floors of basements, except as provided for in Section 1805A.1.1, shall be placed over a floor base course not less than 4 inches (102 mm) in thickness that consists of gravel or crushed stone containing not more than 10 percent of material that passes through a No. 4 (4.75 mm) sieve.

Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a floor base course is not required.

1805A.4.2 Foundation Drain

A drain shall be placed around the perimeter of a foundation that consists of gravel or crushed stone containing not more than 10-percent material that passes through a No. 4 (4.75 mm) sieve. The drain shall extend not less than 12 inches (305 mm) beyond the outside edge of the footing. The thickness shall be such that the bottom of the drain is not higher than the bottom of the base under the floor, and that the top of the drain is not less than 6 inches (152 mm) above the top of the footing. The top of the drain shall be covered with an approved filter membrane material. Where a drain tile or perforated pipe is used, the invert of the pipe or tile shall not be higher than the floor elevation. The top of joints or the top of perforations shall be protected with an approved filter membrane material. The pipe or tile shall be placed on not less than 2 inches (51 mm) of gravel or crushed stone complying with Section 1805.4.1, and shall be covered with not less than 6 inches (152 mm) of the same material.

1805A.4.3 Drainage Discharge

The floor base and foundation perimeter drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the California Plumbing Code.

Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a dedicated drainage system is not required.

Section 1806A Presumptive Load-Bearing Values of Soils

1806A.1 Load Combinations

The presumptive load-bearing values provided in Table 1806A.2 shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605A.2. The values of vertical foundation pressure and lateral bearing pressure given in Table 1806A.2 shall be permitted to be increased by one-third where used with the alternative allowable stress design load combinations of Section 1605A.2 that include wind or earthquake loads.

1806A.2 Presumptive Load-Bearing Values

The load-bearing values used in design for supporting soils and rock near the surface shall not exceed the values specified in Table 1806A.2 unless data to substantiate the use of higher values are submitted and approved. Where the building official has reason to doubt the classification, strength or compressibility of the soil or rock, the requirements of Section 1803A.5.2 shall be satisfied.

Presumptive load-bearing values shall apply to materials with similar physical and engineering characteristics. Mud, organic silt and organic clays (OL, OH), peat (Pt) and undocumented fill shall not be assumed to have a presumptive load-bearing capacity unless data to substantiate the use of such a value are submitted.

Exception: A presumptive load-bearing capacity shall be permitted to be used where the building official deems the load-bearing capacity is adequate for the support of lightweight or temporary structures.

TABLE 1806A.2—PRESUMPTIVE LOAD-BEARING VALUES

| CLASS OF MATERIALS | VERTICAL FOUNDATION PRESSURE (psf) | LATERAL BEARING PRESSURE (psf/ft below natural grade) | LATERAL SLIDING RESISTANCE |  |
| --- | --- | --- | --- | --- |
|  |  |  | Coefficient of frictiona | Cohesion (psf)b |
| 1. Crystalline bedrock | 12,000 | 1,200 | 0.70 | — |
| 2. Sedimentary and foliated rock | 4,000 | 400 | 0.35 | — |
| 3. Sandy gravel and gravel (GW and GP) | 3,000 | 200 | 0.35 | — |
| 4. Sand, silty sand, clayey sand, silty gravel and clayey gravel (SW, SP, SM, SC, GM and GC) | 2,000 | 150 | 0.25 | — |
| 5. Clay, sandy clay, silty clay, clayey silt, silt and sandy silt (CL, ML, MH and CH) | 1,500 | 100 | — | 130 |

For SI: 1 pound per square foot = 0.0479 kPa, 1 pound per square foot per foot = 0.157 kPa/m.

- Coefficient to be multiplied by the dead load.

- Cohesion value to be multiplied by the contact area, as limited by Section 1806A.3.2.

1806A.3 Lateral Load Resistance

Where the presumptive values of Table 1806A.2 are used to determine resistance to lateral loads, the calculations shall be in accordance with Sections 1806A.3.1 through 1806A.3.4.

1806A.3.1 Combined Resistance

The total resistance to lateral loads shall be permitted to be determined by combining the values derived from the lateral bearing pressure and the lateral sliding resistance specified in Table 1806A.2.

1806A.3.2 Lateral Sliding Resistance Limit

For clay, sandy clay, silty clay, clayey silt, silt and sandy silt, the lateral sliding resistance shall not exceed one-half the dead load.

1806A.3.3 Increase for Depth

The lateral bearing pressures specified in Table 1806A.2 shall be permitted to be increased by the tabular value for each additional foot (305 mm) of depth to a value that is not greater than 15 times the tabular value.

1806A.3.4 Increase for Poles

Isolated poles for uses such as flagpoles or signs and poles used to support buildings that are not adversely affected by a 1/2-inch (12.7 mm) motion at the ground surface due to short-term lateral loads shall be permitted to be designed using lateral bearing pressures equal to two times the tabular values.

Section 1807A Foundation Walls, Retaining Walls and Embedded Posts and Poles

1807A.1 Foundation Walls

Foundation walls shall be designed and constructed in accordance with Sections 1807A.1.1 through 1807A.1.6. Foundation walls shall be supported by foundations designed in accordance with Section 1808A.

Building products (4)

FOAMULAR® NGX® 150

Owens Corning

FOAMULAR® NGX® 250

Owens Corning

FOAMULAR® NGX® 400/600/1000

Owens Corning

FOAMULAR® NGX® 404RB/604RB

Owens Corning

1807A.1.1 Design Lateral Soil Loads

Foundation walls shall be designed for the lateral soil loads determined by a geotechnical investigation, in accordance with Section 1803A.

1807A.1.2 Unbalanced Backfill Height

Unbalanced backfill height is the difference in height between the exterior finish ground level and the lower of the top of the concrete footing that supports the foundation wall or the interior finish ground level. Where an interior concrete slab on grade is provided and is in contact with the interior surface of the foundation wall, the unbalanced backfill height shall be permitted to be measured from the exterior finish ground level to the top of the interior concrete slab.

1807A.1.3 Rubble Stone Foundation Walls

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1807A.1.4 Permanent Wood Foundation Systems

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1807A.1.5 Concrete and Masonry Foundation Walls

Concrete and masonry foundation walls shall be designed in accordance with Chapter 19A or 21A, as applicable.

1807A.2 Retaining Walls

Retaining walls shall be designed in accordance with Sections 1807A.2.1 through 1807A.2.4.

1807A.2.1 General

Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and water uplift.

1807A.2.2 Design Lateral Soil Loads

Retaining walls shall be designed for the lateral soil loads determined by a geotechnical investigation in accordance with Section 1803A and shall not be less than eighty percent of the lateral soil loads determined in accordance with Section 1610A. For use with the load combinations, lateral soil loads due to gravity loads surcharge shall be considered gravity loads and seismic earth pressure increases due to earthquake shall be considered as seismic loads. For structures assigned to Seismic Design Category D, E or F, the design of retaining walls supporting more than 6 feet (1829 mm) of backfill height shall incorporate the additional seismic lateral earth pressure in accordance with the geotechnical investigation where required in Section 1803A.2.

1807A.2.3 Safety Factor

Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605A shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall.

Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.

1807A.2.4 Segmental Retaining Walls

Dry-cast concrete units used in the construction of segmental retaining walls shall comply with ASTM C1372.

1807A.2.5 Guards

Guards shall be provided at retaining walls in accordance with Sections 1807A.2.5.1 through 1807A.2.5.3.

Exception: Guards are not required at retaining walls not accessible to the public.

1807A.2.5.1 Where Required

At retaining walls located within 36 inches (914mm) of walking surfaces, a guard shall be required between the walking surface and the open side of the retaining wall where the walking surface is located more than 30 inches (762 mm) measured vertically to the surface or grade below at any point within 36 inches (914mm) horizontally to the edge of the open side. Guards shall comply with Section 1607A.9.

1807A.2.5.2 Height

Required guards at retaining walls shall comply with the height requirements of Section 1015.3.

1807A.2.5.3 Opening Limitations

Required guards shall comply with the opening limitations of Section 1015.4.

1807A.3 Embedded Posts and Poles

Designs to resist both axial and lateral loads employing posts or poles as columns embedded in earth or in concrete footings in earth shall be in accordance with Sections 1807A.3.1 through 1807A.3.3 or ASABE EP 486.3 Chapter 8 using soil properties and acceptance criteria determined by the geotechnical engineer in accordance with Section 1803A.

1807A.3.1 Limitations

The design procedures outlined in this section are subject to the following limitations:

- The frictional resistance for structural walls and slabs on silts and clays shall be limited to one-half of the normal force imposed on the soil by the weight of the footing or slab.

- Posts embedded in earth shall not be used to provide lateral support for structural or nonstructural materials such as plaster, masonry or concrete unless bracing is provided that develops the limited deflection required.

Wood poles shall be treated in accordance with AWPA U1 for sawn timber posts (Commodity Specification A, Use Category 4B) and for round timber posts (Commodity Specification B, Use Category 4B).

1807A.3.2 Design Criteria

The depth to resist lateral loads shall be determined using the design criteria established in Sections 1807A.3.2.1 through 1807A.3.2.3, or by other methods approved by the building official.

1807A.3.2.1 Nonconstrained

The following formula shall be used in determining the depth of embedment required to resist lateral loads where lateral constraint is not provided at the ground surface, such as by a rigid floor or rigid ground surface pavement, and where lateral constraint is not provided above the ground surface, such as by a structural diaphragm.

Equation 18A-1

where:

A = 2.34P/(S1b).

b = Diameter of round post or footing or diagonal dimension of square post or footing, feet (m).

d = Depth of embedment in earth in feet (m) but not over 12 feet (3658 mm) for purpose of computing lateral pressure.

h = Distance in feet (m) from ground surface to point of application of "P."

P = Applied lateral force in pounds (kN).

S1 = Allowable lateral soil-bearing pressure as set forth in Section 1806A.2 based on a depth of one-third the depth of embedment in pounds per square foot (psf) (kPa).

1807A.3.2.2 Constrained

The following formula shall be used to determine the depth of embedment required to resist lateral loads where lateral constraint is provided at the ground surface, such as by a rigid floor or slab-on-ground.

Equation 18A-2

or alternatively

Equation 18A-3

where:

Mg = Moment in the post at grade, in foot-pounds (kN-m).

S3 = Allowable lateral soil-bearing pressure as set forth in Section 1806.2 based on a depth equal to the depth of embedment in pounds per square foot (kPa).

1807A.3.2.3 Vertical Load

The resistance to vertical loads shall be determined using the vertical foundation pressure set forth in Table 1806A.2.

1807A.3.3 Backfill

The backfill in the annular space around columns not embedded in poured footings shall be by one of the following methods:

- Backfill shall be of concrete with a specified compressive strength of not less than 2,000 psi (13.8 MPa). The hole shall be not less than 4 inches (102 mm) larger than the diameter of the column at its bottom or 4 inches (102 mm) larger than the diagonal dimension of a square or rectangular column.

- Backfill shall be of clean sand. The sand shall be thoroughly compacted by tamping in layers not more than 8 inches (203 mm) in depth.

- Backfill shall be of controlled low-strength material (CLSM).

Section 1808A Foundations

1808A.1 General

Foundations shall be designed and constructed in accordance with Sections 1808A.2 through 1808A.9. Shallow foundations shall satisfy the requirements of Section 1809A. Deep foundations shall satisfy the requirements of Section 1810A.

1808A.2 Design for Capacity and Settlement

Foundations shall be so designed that the allowable bearing capacity of the soil is not exceeded, and that differential settlement is minimized. Foundations in areas with expansive soils shall be designed in accordance with the provisions of Section 1808A.6.

The enforcing agency may require an analysis of foundation elements to determine subgrade deformations in order to evaluate their effect on the superstructure, including story drift.

1808A.3 Design Loads

Foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 2.3 or 2.4 of ASCE 7 or the alternative allowable stress design load combinations of Section 1605A.2. The dead load is permitted to include the weight of foundations and overlying fill. Reduced live loads, as specified in Sections 1607A.13 and 1607A.14, shall be permitted to be used in the design of foundations.

1808A.3.1 Seismic Overturning

Where foundations are proportioned using the load combinations of Section 2.3 or 2.4 of ASCE 7 and the computation of seismic over-turning effects is by equivalent lateral force analysis or modal analysis, the proportioning shall be in accordance with Section 12.13.4 of ASCE 7.

1808A.3.2 Surcharge

Fill or other surcharge loads shall not be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or the surcharge. Existing footings or foundations that will be affected by any excavation shall be underpinned or otherwise protected against settlement and shall be protected against detrimental lateral or vertical movement or both.

Exception: Minor grading for landscaping purposes shall be permitted where done with walk-behind equipment, where the grade is not increased more than 1 foot (305 mm) from original design grade or where approved by the building official.

1808A.4 Vibratory Loads

Where machinery operations or other vibrations are transmitted through the foundation, consideration shall be given in the foundation design to prevent detrimental disturbances of the soil.

1808A.5 Shifting or Moving Soils

Where it is known that the shallow subsoils are of a shifting or moving character, foundations shall be carried to a sufficient depth to ensure stability.

1808A.6 Design for Expansive Soils

Foundations for buildings and structures founded on expansive soils shall be designed in accordance with Section 1808A.6.1 or 1808A.6.2.

Exceptions: Foundation design need not comply with Section 1808A.6.1 or 1808A.6.2 where one of the following conditions is satisfied:

- The soil is removed in accordance with Section 1808A.6.3.

- The building official approves stabilization of the soil in accordance with Section 1808A.6.4.

1808A.6.1 Foundations

Foundations placed on or within the active zone of expansive soils shall be designed to resist differential volume changes and to prevent structural damage to the supported structure. Deflection and racking of the supported structure shall be limited to that which will not interfere with the usability and serviceability of the structure.

Foundations placed below where volume change occurs or below expansive soil shall comply with the following provisions:

- Foundations extending into or penetrating expansive soils shall be designed to prevent uplift of the supported structure.

- Foundations penetrating expansive soils shall be designed to resist forces exerted on the foundation due to soil volume changes or shall be isolated from the expansive soil.

1808A.6.2 Slab-on-Ground Foundations

Moments, shears and deflections for use in designing slab-on-ground, mat or raft foundations on expansive soils shall be determined in accordance with WRI/CRSI or PTI DC 10.5. Using the moments, shears and deflections determined above, nonprestressed slabs-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with WRI/CRSI and post-tensioned slabs-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with PTI DC 10.5. It shall be permitted to analyze and design such slabs by other methods that account for soil-structure interaction, the deformed shape of the soil support, the plate or stiffened plate action of the slab as well as both center lift and edge lift conditions. Such alternative methods shall be rational and the basis for all aspects and parameters of the method shall be available for peer review.

1808A.6.3 Removal of Expansive Soil

Where expansive soil is removed in lieu of designing foundations in accordance with Section 1808A.6.1 or 1808A.6.2, the soil shall be removed to a depth sufficient to ensure a constant moisture content in the remaining soil. Fill material shall not contain expansive soils and shall comply with Section 1804A.5 or 1804A.6.

Exception: Expansive soil need not be removed to the depth of constant moisture, provided that the confining pressure in the expansive soil created by the fill and supported structure exceeds the swell pressure.

1808A.6.4 Stabilization

Where the active zone of expansive soils is stabilized in lieu of designing foundations in accordance with Section 1808A.6.1 or 1808A.6.2, the soil shall be stabilized by chemical, dewatering, presaturation or equivalent techniques.

1808A.7 Foundations on or Adjacent to Slopes

The placement of buildings and structures on or adjacent to slopes steeper than one unit vertical in three units horizontal (33.3-percent slope) shall comply with Sections 1808A.7.1 through 1808A.7.5.

1808A.7.1 Building Clearance From Ascending Slopes

In general, buildings below slopes shall be set a sufficient distance from the slope to provide protection from slope drainage, erosion and shallow failures. Except as provided in Section 1808A.7.5 and Figure 1808A.7.1, the following criteria will be assumed to provide this protection. Where the existing slope is steeper than one unit vertical in one unit horizontal (100-percent slope), the toe of the slope shall be assumed to be at the intersection of a horizontal plane drawn from the top of the foundation and a plane drawn tangent to the slope at an angle of 45 degrees (0.79 rad) to the horizontal. Where a retaining wall is constructed at the toe of the slope, the height of the slope shall be measured from the top of the wall to the top of the slope.

FIGURE 1808A.7.1—FOUNDATION CLEARANCES FROM SLOPES

For SI: 1 foot = 304.8 mm.

1808A.7.2 Foundation Setback From Descending Slope Surface

Foundations on or adjacent to slope surfaces shall be founded in firm material with an embedment and set back from the slope surface sufficient to provide vertical and lateral support for the foundation without detrimental settlement. Except as provided for in Section 1808A.7.5 and Figure 1808A.7.1, the following setback is deemed adequate to meet the criteria. Where the slope is steeper than 1 unit vertical in 1 unit horizontal (100-percent slope), the required setback shall be measured from an imaginary plane 45 degrees (0.79 rad) to the horizontal, projected upward from the toe of the slope.

1808A.7.3 Pools

Diagram

The setback between pools regulated by this code and slopes shall be equal to one-half the building footing setback distance required by this section. That portion of the pool wall within a horizontal distance of 7 feet (2134 mm) from the top of the slope shall be capable of supporting the water in the pool without soil support.

UpCodes Diagram (1)

Pool Enclosures and Gates

1808A.7.4 Foundation Elevation

On graded sites, the top of any exterior foundation shall extend above the elevation of the street gutter at point of discharge or the inlet of an approved drainage device not less than 12 inches (305 mm) plus 2 percent. Alternate elevations are permitted subject to the approval of the building official, provided that it can be demonstrated that required drainage to the point of discharge and away from the structure is provided at all locations on the site.

1808A.7.5 Alternate Setback and Clearance

Alternate setbacks and clearances are permitted, subject to the approval of the building official. The building official shall be permitted to require a geotechnical investigation as set forth in Section 1803A.5.10.

1808A.8 Concrete Foundations

The design, materials and construction of concrete foundations shall comply with Sections 1808A.8.1 through 1808A.8.6 and the provisions of Chapter 19A.

1808A.8.1 Concrete or Grout Strength and Mix Proportioning

Concrete or grout in foundations shall have a specified compressive strength (f 'c) not less than the largest applicable value indicated in Table 1808A.8.1.

Where concrete or grout is to be pumped, the mix design including slump shall be adjusted to produce a pumpable mixture.

TABLE 1808A.8.1—MINIMUM SPECIFIED COMPRESSIVE STRENGTH f 'c OF CONCRETE OR GROUT

| FOUNDATION ELEMENT OR CONDITION | SPECIFIED COMPRESSIVE STRENGTH, f 'c |
| --- | --- |
| 1. Foundations for structures assigned to Seismic Design Category D, E or F | 3,000 psi |
| 2. Precast nonprestressed driven piles | 4,000 psi |
| 3. Socketed drilled shafts | 4,000 psi |
| 4. Micropiles | 4,000 psi |
| 5. Precast prestressed driven piles | 5,000 psi |

For SI: 1 pound per square inch = 0.00689 MPa.

1808A.8.2 Concrete Cover

The concrete cover provided for prestressed and nonprestressed reinforcement in foundations shall be not less than the largest applicable value specified in Table 1808A.8.2. Longitudinal bars spaced less than 11/2 inches (38 mm) clear distance apart shall be considered to be bundled bars for which the concrete cover provided shall be not less than that required by Section 20.5.1.3.5 of ACI 318. Concrete cover shall be measured from the concrete surface to the outermost surface of the steel to which the cover requirement applies. Where concrete is placed in a temporary or permanent casing or a mandrel, the inside face of the casing or mandrel shall be considered to be the concrete surface.

TABLE 1808A.8.2—MINIMUM CONCRETE COVER

| FOUNDATION ELEMENT OR CONDITION | MINIMUM COVER |
| --- | --- |
| 1. Shallow foundations | In accordance with Section 20.5 of ACI 318 |
| 2. Precast nonprestressed deep foundation elements |  |
| Exposed to seawater | 3 inches |
| Not manufactured under plant conditions | 2 inches |
| Manufactured under plant control conditions | In accordance with Section 20.5.1.3.3 of ACI 318 |
| 3. Precast prestressed deep foundation elements |  |
| Exposed to seawater | 2.5 inches |
| Other | In accordance with Section 20.5.1.3.3 of ACI 318 |
| 4. Cast-in-place deep foundation elements not enclosed by a steel pipe, tube or permanent casing | 2.5 inches |
| 5. Cast-in-place deep foundation elements enclosed by a steel pipe, tube or permanent casing | 1 inch |
| 6. Structural steel core within a steel pipe, tube or permanent casing | 2 inches |
| 7. Cast-in-place drilled shafts enclosed by a stable rock socket | 1.5 inches |

For SI: 1 inch = 25.4 mm.

1808A.8.3 Placement of Concrete

Concrete shall be placed in such a manner as to ensure the exclusion of any foreign matter and to secure a full-size foundation. Concrete shall not be placed through water unless a tremie or other method approved by the building official is used. Where placed under or in the presence of water, the concrete shall be deposited by approved means to ensure minimum segregation of the mix and negligible turbulence of the water. Where depositing concrete from the top of a deep foundation element, the concrete shall be chuted directly into smooth-sided pipes or tubes or placed in a rapid and continuous operation through a funnel hopper centered at the top of the element.

1808A.8.4 Protection of Concrete

Concrete foundations shall be protected from freezing during depositing and for a period of not less than 5 days thereafter. Water shall not be allowed to flow through the deposited concrete.

1808A.8.5 Forming of Concrete

Concrete foundations are permitted to be cast against the earth where, in the opinion of the building official, soil conditions do not require formwork. Where formwork is required, it shall be in accordance with Section 26.11 of ACI 318.

1808A.8.6 Seismic Requirements

See Section 1905A for additional requirements for foundations of structures assigned to Seismic Design Category D, E or F.

For structures assigned to Seismic Design Category D, E or F, provisions of Section 18.13 of ACI 318 shall apply where not in conflict with the provisions of Sections 1808A through 1810A.

1808A.9 Vertical Masonry Foundation Elements

Vertical masonry foundation elements that are not foundation piers as defined in Section 202 shall be designed as piers, walls or columns, as applicable, in accordance with TMS 402.

Section 1809A Shallow Foundations

1809A.1 General

Shallow foundations shall be designed and constructed in accordance with Sections 1809A.2 through 1809A.15.

1809A.2 Supporting Soils

Shallow foundations shall be built on undisturbed soil, compacted fill material or controlled low-strength material (CLSM). Compacted fill material shall be placed in accordance with Section 1804A.6. CLSM shall be placed in accordance with Section 1804A.7.

1809A.3 Stepped Footings

The top surface of footings shall be level. The bottom surface of footings shall be permitted to have a slope not exceeding 1 unit vertical in 10 units horizontal (10-percent slope). Footings shall be stepped where it is necessary to change the elevation of the top surface of the footing or where the surface of the ground slopes more than 1 unit vertical in 10 units horizontal (10-percent slope).

Individual steps in continuous footings shall not exceed 18 inches (457 mm) in height and the slope of a series of such steps shall not exceed 1 unit vertical to 2 units horizontal (50 percent slope) unless otherwise recommended by a geotechnical report. The steps shall be detailed on the drawings. The local effects due to the discontinuity of the steps shall be considered in the design of the foundation.

1809A.4 Depth and Width of Footings

The minimum depth of footings below the undisturbed ground surface shall be 12 inches (305 mm). Where applicable, the requirements of Section 1809A.5 shall be satisfied. The minimum width of footings shall be 12 inches (305 mm).

1809A.5 Frost Protection

Except where otherwise protected from frost, foundations and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods:

- Extending below the frost line of the locality.

- Constructing in accordance with ASCE 32.

- Erecting on solid rock.

Exception: Free-standing buildings meeting all of the following conditions shall not be required to be protected:

  - Assigned to Risk Category I.

  - Area of 600 square feet (56 m2) or less for light-frame construction or 400 square feet (37 m2) or less for other than light-frame construction.

  - Eave height of 10 feet (3048 mm) or less.

Shallow foundations shall not bear on frozen soil unless such frozen condition is of a permanent character.

1809A.5.1 Frost Protection at Required Exits

Frost protection shall be provided at exterior landings for all required exits with outward-swinging doors. Frost protection shall only be required to the extent necessary to ensure the unobstructed opening of the required exit doors.

1809A.6 Location of Footings

Footings on granular soil shall be so located that the line drawn between the lower edges of adjacent footings shall not have a slope steeper than 30 degrees (0.52 rad) with the horizontal, unless the material supporting the higher footing is braced or retained or otherwise laterally supported in an approved manner or a greater slope has been properly established by engineering analysis.

1809A.7 Prescriptive Footings for Light-Frame Construction

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1809A.8 Plain Concrete Footings

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1809A.9 Masonry-Unit Footings

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1809A.10 Pier and Curtain Wall Foundations

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1809A.11 Steel Grillage Footings

Grillage footings of structural steel elements shall be separated with approved steel spacers and be entirely encased in concrete with not less than 6 inches (152 mm) on the bottom and not less than 4 inches (102 mm) at all other points. The spaces between the shapes shall be completely filled with concrete or cement grout.

1809A.12 Timber Footings

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1809A.13 Footing Seismic Ties

Where a structure is assigned to Seismic Design Category D, E or F, individual spread footings founded on soil defined in Chapter 20 of ASCE 7 as Site Class E or F shall be interconnected by ties. Unless it is demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade or reinforced concrete slabs on grade, ties shall be capable of carrying, in tension or compression, a force equal to the lesser of the product of the larger footing design gravity load times the seismic coefficient, SDS, divided by 10 and 25 percent of the smaller footing design gravity load.

1809A.14 Grade Beams

Grade beams shall comply with the provisions of ACI 318.

Exception: Grade beams not subject to differential settlement exceeding one-fourth of the thresholds specified in ASCE 7 Table 12.13-3 and designed to resist the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 need not comply with ACI 318 Section 18.13.3.1.

1809A.15 Pipes and Trenches

Unless otherwise recommended by the soils report, open or backfilled trenches parallel with a footing shall not be below a plane having a downward slope of 1 unit vertical to 2 units horizontal (50 percent slope) from a line 9 inches (229 mm) above the bottom edge of the footing, and not closer than 18 inches (457 mm) from the face of such footing.

Where pipes cross under footings, the footings shall be specially designed. Pipe sleeves shall be provided where pipes cross through footings or footing walls and sleeve clearances shall provide for possible footing settlement, but not less than 1 inch (25 mm) all around pipe.

Exception: Alternate trench locations and pipe clearances shall be permitted when approved by registered design professional and the enforcement agent.

Section 1810A Deep Foundations

1810A.1 General

Deep foundations shall be analyzed, designed, detailed and installed in accordance with Sections 1810A.1 through 1810A.4.

1810A.1.1 Geotechnical Investigation

Deep foundations shall be designed and installed on the basis of a geotechnical investigation as set forth in Section 1803A.

1810A.1.2 Use of Existing Deep Foundation Elements

Deep foundation elements left in place where a structure has been demolished shall not be used for the support of new construction unless satisfactory evidence is submitted to the building official, which indicates that the elements are sound and meet the requirements of this code. Such elements shall be load tested or redriven to verify their capacities. The design load applied to such elements shall be the lowest allowable load as determined by tests or redriving data.

1810A.1.3 Deep Foundation Elements Classified as Columns

Deep foundation elements standing unbraced in air, water or fluid soils shall be classified as columns and designed as such in accordance with the provisions of this code from their top down to the point where adequate lateral support is provided in accordance with Section 1810A.2.1.

Exception: Where the unsupported height to least horizontal dimension of a cast-in-place deep foundation element does not exceed three, it shall be permitted to design and construct such an element as a pedestal in accordance with ACI 318.

1810A.1.4 Special Types of Deep Foundations

The use of types of deep foundation elements not specifically mentioned herein is permitted, subject to the approval of the building official, upon the submission of acceptable test data, calculations and other information relating to the structural properties and load capacity of such elements. The allowable stresses for materials shall not in any case exceed the limitations specified herein.

1810A.2 Analysis

The analysis of deep foundations for design shall be in accordance with Sections 1810A.2.1 through 1810A.2.5.

1810A.2.1 Lateral Support

Any soil other than fluid soil shall be deemed to afford sufficient lateral support to prevent buckling of deep foundation elements and to permit the design of the elements in accordance with accepted engineering practice and the applicable provisions of this code.

Where deep foundation elements stand unbraced in air, water or fluid soils, it shall be permitted to consider them laterally supported at a point 5 feet (1524 mm) into stiff soil or 10 feet (3048 mm) into soft soil unless otherwise approved by the building official on the basis of a geotechnical investigation by a registered design professional.

1810A.2.2 Stability

Deep foundation elements shall be braced to provide lateral stability in all directions. Three or more elements connected by a rigid cap shall be considered to be braced, provided that the elements are located in radial directions from the centroid of the group not less than 60 degrees (1 rad) apart. A two-element group in a rigid cap shall be considered to be braced along the axis connecting the two elements. Methods used to brace deep foundation elements shall be subject to the approval of the building official.

Deep foundation elements supporting walls shall be placed alternately in lines spaced not less than 1 foot (305 mm) apart and located symmetrically under the center of gravity of the wall load carried, unless effective measures are taken to provide for eccentricity and lateral forces, or the foundation elements are adequately braced to provide for lateral stability.

Exceptions:

- Isolated cast-in-place deep foundation elements without lateral bracing shall be permitted where the least horizontal dimension is not less than 2 feet (610 mm), adequate lateral support in accordance with Section 1810A.2.1 is provided for the entire height and analysis demonstrates that the element can support the required loads, including mislocations required by Section 1810A.3.1.3, with neither harmful distortion nor instability in the structure.

- A single row of deep foundation elements without lateral bracing is permitted for one- and two-family dwellings and lightweight construction not exceeding two stories above grade plane or 35 feet (10 668 mm) in building height, provided that the centers of the elements are located within the width of the supported wall.

1810A.2.3 Settlement

The settlement of a single deep foundation element or group thereof shall be estimated based on approved methods of analysis. The predicted settlement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity.

1810A.2.4 Lateral Loads

The moments, shears and lateral deflections used for design of deep foundation elements shall be established considering the nonlinear interaction of the shaft and soil, as determined by a registered design professional. Where the ratio of the depth of embedment of the element to its least horizontal dimension is less than or equal to six, it shall be permitted to assume the element is rigid.

1810A.2.4.1 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, deep foundation elements on Site Class E or F sites, as determined in Section 1613A.2.2, shall be designed and constructed to withstand maximum imposed curvatures from earthquake ground motions and structure response. Curvatures shall include free-field soil strains modified for soil-foundation-structure interaction coupled with foundation element deformations associated with earthquake loads imparted to the foundation by the structure.

Exception: Deep foundation elements that satisfy the following additional detailing requirements shall be deemed to comply with the curvature capacity requirements of this section:

- Precast prestressed concrete piles detailed in accordance with Section 1810A.3.8.

- Cast-in-place deep foundation elements with a minimum longitudinal reinforcement ratio of 0.005 extending the full length of the element and detailed in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 as required by Section 1810A.3.9.4.2.2.

1810A.2.5 Group Effects

The analysis shall include group effects on lateral behavior where the center-to-center spacing of deep foundation elements in the direction of lateral force is less than eight times the least horizontal dimension of an element. The analysis shall include group effects on axial behavior where the center-to-center spacing of deep foundation elements is less than three times the least horizontal dimension of an element. Group effects shall be evaluated using a generally accepted method of analysis; the analysis for uplift of grouped elements with center-to-center spacing less than three times the least horizontal dimension of an element shall be evaluated in accordance with Section 1810A.3.3.1.6.

1810A.3 Design and Detailing

Deep foundations shall be designed and detailed in accordance with Sections 1810A.3.1 through 1810A.3.13.

1810A.3.1 Design Conditions

Design of deep foundations shall include the design conditions specified in Sections 1810A.3.1.1 through 1810A.3.1.6, as applicable.

1810A.3.1.1 Design Methods for Concrete Elements

Where concrete deep foundations are laterally supported in accordance with Section 1810A.2.1 for the entire height and applied forces cause bending moments not greater than those resulting from accidental eccentricities, structural design of the element using the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605A.2 and the allowable stresses specified in this chapter shall be permitted. Otherwise, the structural design of concrete deep foundation elements shall use the strength load combinations specified in ASCE 7, Section 2.3 and approved strength design methods.

1810A.3.1.2 Composite Elements

Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section of the composite assembly shall satisfy the applicable requirements of this code, and the maximum allowable load in each section shall be limited by the structural capacity of that section.

1810A.3.1.3 Mislocation

The foundation or superstructure shall be designed to resist the effects of the mislocation of any deep foundation element by not less than 3 inches (76 mm). To resist the effects of mislocation, compressive overload of deep foundation elements to 110 percent of the allowable design load shall be permitted.

1810A.3.1.4 Driven Piles

Driven piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.

1810A.3.1.5 Helical Piles

Helical piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by installation into the ground and service loads.

1810A.3.1.5.1 Helical Piles Seismic Requirements

For structures assigned to Seismic Design Category D, E or F, capacities of helical piles shall be determined in accordance with Section 1810A.3.3 by at least two project-specific preproduction tests for each soil profile, size and depth of helical pile. At least two percent of all production piles shall be proof tested to the load determined in accordance with Section 1617A.1.15.

Helical piles shall satisfy corrosion resistance requirements of ICC-ES AC 358. In addition, all helical pile materials that are subject to corrosion shall include at least 1/16-inch corrosion allowance.

Helical piles shall not be considered as carrying any horizontal loads.

1810A.3.1.6 Casings

Temporary and permanent casings shall be of steel and shall be sufficiently strong to resist collapse and sufficiently watertight to exclude any foreign materials during the placing of concrete. Where a permanent casing is considered reinforcing steel, the steel shall be protected under the conditions specified in Section 1810A.3.2.5. Horizontal joints in the casing shall be spliced in accordance with Section 1810A.3.6.

1810A.3.2 Materials

The materials used in deep foundation elements shall satisfy the requirements of Sections 1810A.3.2.1 through 1810A.3.2.8, as applicable.

1810A.3.2.1 Concrete

Where concrete is cast in a steel pipe or where an enlarged base is formed by compacting concrete, the maximum size for coarse aggregate shall be 3/4 inch (19.1 mm). Concrete to be compacted shall have a zero slump.

1810A.3.2.1.1 Seismic Hooks

For structures assigned to Seismic Design Category C, D, E or F, the ends of hoops, spirals and ties used in concrete deep foundation elements shall be terminated with seismic hooks, as defined in ACI 318, and shall be turned into the confined concrete core.

1810A.3.2.2 Prestressing Steel

Prestressing steel shall conform to ASTM A416.

1810A.3.2.3 Steel

Structural steel H-piles and structural steel sheet piling shall conform to the material requirements in ASTM A6. Steel pipe piles shall conform to the material requirements in ASTM A252. Fully welded steel piles shall be fabricated from plates that conform to the material requirements in ASTM A36, ASTM A283, ASTM A572, ASTM A588 or ASTM A690.

1810A.3.2.4 Timber

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1810A.3.2.5 Protection of Materials

Where boring records or site conditions indicate possible deleterious action on the materials used in deep foundation elements because of soil constituents, changing water levels or other factors, the elements shall be adequately protected by materials, methods or processes approved by the building official. Protective materials shall be applied to the elements so as not to be rendered ineffective by installation. The effectiveness of such protective measures for the particular purpose shall have been thoroughly established by satisfactory service records or other evidence.

1810A.3.2.6 Allowable Stresses

The allowable stresses for materials used in deep foundation elements shall not exceed those specified in Table 1810A.3.2.6.

TABLE 1810A.3.2.6—ALLOWABLE STRESSES FOR MATERIALS USED IN DEEP FOUNDATION ELEMENTS

| MATERIAL TYPE AND CONDITION | MAXIMUM ALLOWABLE STRESSa |
| --- | --- |
| 1. Concrete or grout in compressionb |  |
| Cast-in-place with a permanent casing in accordance with Section 1810A.3.2.7 or Section 1810A.3.5.3.4 | 0.4 f 'c |
| Cast-in-place in other permanent casing or rock | 0.33 f 'c |
| Cast-in-place without a permanent casing | 0.3 f 'c |
| Precast nonprestressed | 0.33 f 'c |
| Precast prestressed | 0.33 f 'c - 0.27 fpc |
| 2. Nonprestressed reinforcement in compression | 0.4 fy ≤ 30,000 psi |
| 3. Steel in compression |  |
| Cores within concrete-filled pipes or tubes | 0.5 Fy ≤ 32,000 psi |
| Pipes, tubes or H-piles, where justified in accordance with Section 1810.3.2.8 | 0.5 Fy ≤ 32,000 psi |
| Pipes or tubes for micropiles | 0.4 Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35 Fy ≤ 24,000 psi |
| Helical piles | 0.6 Fy ≤ 0.5 Fu |
| 4. Nonprestressed reinforcement in tension |  |
| Within micropiles | 0.6 fy |
| Other conditions |  |
| For load combinations that do not include wind or seismic loads | 0.5 fy ≤ 30,000 psi |
| For load combinations that include wind or seismic loads | 0.5 fy ≤ 40,000 psi |
| 5. Steel in tension |  |
| Pipes, tubes or H-piles, where justified in accordance with Section 1810.3.2.8 | 0.5 Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35 Fy ≤ 24,000 psi |
| Helical piles | 0.6 Fy ≤ 0.5 Fu |
| 6. Timber | In accordance with the ANSI/AWC NDS |

- f 'c is the specified compressive strength of the concrete or grout; fpc is the compressive stress on the gross concrete section due to effective prestress forces only; fy is the specified yield strength of reinforcement; Fy is the specified minimum yield stress of steel; Fu is the specified minimum tensile stress of structural steel.

- The stresses specified apply to the gross cross-sectional area of the concrete for precast prestressed piles and to the net cross-sectional area for all other piles. Where a temporary or permanent casing is used, the inside face of the casing shall be considered the outer edge of the concrete cross-section.

1810A.3.2.7 Increased Allowable Compressive Stress for Cased Mandrel-Driven Cast-in-Place Elements

The allowable compressive stress in the concrete shall be permitted to be increased as specified in Table 1810A.3.2.6 for those portions of permanently cased cast-in-place elements that satisfy all of the following conditions:

- The design shall not use the casing to resist any portion of the axial load imposed.

- The casing shall have a sealed tip and be mandrel driven.

- The thickness of the casing shall be not less than manufacturer's standard gage No. 14 (0.068 inch) (1.75 mm).

- The casing shall be seamless or provided with seams of strength equal to the basic material and be of a configuration that will provide confinement to the cast-in-place concrete.

- The ratio of steel yield strength (Fy) to specified compressive strength (f 'c) shall be not less than six.

- The nominal diameter of the element shall not be greater than 16 inches (406 mm).

1810A.3.2.8 Justification of Higher Allowable Stresses

Use of allowable stresses in Table 1810A.3.2.6 that must be justified in accordance with this section shall be permitted where supporting data justifying such higher stresses is submitted to and approved by the building official. Such substantiating data shall include the following:

- A geotechnical investigation in accordance with Section 1803A.

- Load tests in accordance with Section 1810A.3.3.1.2, regardless of the load supported by the element.

The design and installation of the deep foundation elements shall be under the direct supervision of a registered design professional knowledgeable in the field of soil mechanics and deep foundations who shall submit a report to the building official stating that the elements as installed satisfy the design criteria.

1810A.3.3 Determination of Allowable Loads

The allowable axial and lateral loads on deep foundation elements shall be determined by an approved formula, load tests or method of analysis.

1810A.3.3.1 Allowable Axial Load

The allowable axial load on a deep foundation element shall be determined in accordance with Sections 1810A.3.3.1.1 through 1810A.3.3.1.9.

Exception: Where approved by the building official, load testing is not required.

1810A.3.3.1.1 Driving Criteria

The allowable compressive load on any driven deep foundation element where determined by the application of an approved driving formula shall not exceed 40 tons (356 kN). For allowable loads above 40 tons (356 kN), the wave equation method of analysis shall be used to estimate driveability for both driving stresses and net displacement per blow at the ultimate load. Allowable loads shall be verified by load tests in accordance with Section 1810A.3.3.1.2. The formula or wave equation load shall be determined for gravity-drop or power-actuated hammers and the hammer energy used shall be the maximum consistent with the size, strength and weight of the driven elements. The use of a follower is permitted only with the approval of the building official. The introduction of fresh hammer cushion or pile cushion material just prior to final penetration is not permitted.

1810A.3.3.1.2 Load Tests

Where design compressive loads are greater than those determined using the allowable stresses specified in Section 1810A.3.2.6, where the design load for any deep foundation element is in doubt, where driven deep foundation elements are installed by means other than a pile hammer, or where cast-in-place deep foundation elements have an enlarged base formed either by compacting concrete or by driving a precast base, control test elements shall be tested in accordance with ASTM D1143 or ASTM D4945. One element or more shall be load tested in each area of uniform subsoil conditions. Where required by the building official, additional elements shall be load tested where necessary to establish the safe design capacity. The resulting allowable loads shall not be more than one-half of the ultimate axial load capacity of the test element as assessed by one of the published methods listed in Section 1810A.3.3.1.3 with consideration for the test type, duration and subsoil. The ultimate axial load capacity shall be determined by a registered design professional with consideration given to tolerable total and differential settlements at design load in accordance with Section 1810A.2.3. In subsequent installation of the balance of deep foundation elements, all elements shall be deemed to have a supporting capacity equal to that of the control element where such elements are of the same type, size and relative length as the test element; are installed using the same or comparable methods and equipment as the test element; are installed in similar subsoil conditions as the test element; and, for driven elements, where the rate of penetration (for example, net displacement per blow) of such elements is equal to or less than that of the test element driven with the same hammer through a comparable driving distance, or where the downward pressure and torque on such elements is greater than or equal to that applied to the test element that determined the ultimate axial load capacity at a comparable driving distance.

1810A.3.3.1.3 Load Test Evaluation Methods

It shall be permitted to evaluate load tests of deep foundation elements using any of the following methods:

- Davisson Offset Limit.

- Brinch-Hansen 90-percent Criterion.

- Butler-Hoy Criterion.

- Other methods approved by the building official.

1810A.3.3.1.4 Allowable Shaft Resistance

The assumed shaft resistance developed by any uncased cast-in-place deep foundation element shall not exceed one-sixth of the bearing value of the soil material at minimum depth as set forth in Table 1806A.2, up to 500 psf (24 kPa), unless a greater value is allowed by the building official on the basis of a geotechnical investigation as specified in Section 1803A or a greater value is substantiated by a load test in accordance with Section 1810A.3.3.1.2. Shaft resistance and end-bearing resistance shall not be assumed to act simultaneously unless determined by a geotechnical investigation in accordance with Section 1803A.

1810A.3.3.1.5 Uplift Capacity of a Single Deep Foundation Element

Where required by the design, the uplift capacity of a single deep foundation element shall be determined by an approved method of analysis based on a minimum factor of safety of three or by load tests conducted in accordance with ASTM D3689. The maximum allowable uplift load shall not exceed the ultimate load capacity as determined in Section 1810A.3.3.1.2, using the results of load tests conducted in accordance with ASTM D3689 divided by a factor of safety of two.

Exception: Where uplift is due to wind or seismic loading, the minimum factor of safety shall be two where capacity is determined by an analysis and one and one-half where capacity is determined by load tests.

1810A.3.3.1.6 Allowable Uplift Load of Grouped Deep Foundation Elements

For grouped deep foundation elements subjected to uplift, the allowable uplift load for the group shall be calculated by a generally accepted method of analysis. Where the deep foundation elements in the group are placed at a center-to-center spacing less than three times the least horizontal dimension of the largest single element, the allowable uplift load for the group is permitted to be calculated as the lesser of:

- The proposed individual allowable uplift load times the number of elements in the group.

- Two-thirds of the effective weight of the group and the soil contained within a block defined by the perimeter of the group and the length of the element, plus two-thirds of the ultimate shear resistance along the soil block.

1810A.3.3.1.7 Load-Bearing Capacity

Deep foundation elements shall develop ultimate load capacities of not less than twice the design working loads in the designated load-bearing layers. Analysis shall show that soil layers underlying the designated load-bearing layers do not cause the load-bearing capacity safety factor to be less than two.

1810A.3.3.1.8 Bent Deep Foundation Elements

The load-bearing capacity of deep foundation elements discovered to have a sharp or sweeping bend shall be determined by an approved method of analysis or by load testing a representative element.

1810A.3.3.1.9 Helical Piles

The allowable axial design load, Pa, of helical piles shall be determined as follows:

Equation 18A-4

where Pu is the least value of:

- Base capacity plus shaft resistance of the helical pile. The base capacity is equal to the sum of the areas of the helical bearing plates times the ultimate bearing capacity of the soil or rock comprising the bearing stratum. The shaft resistance is equal to the area of the shaft above the uppermost helical bearing plate times the ultimate skin resistance.

- Ultimate capacity determined from well-documented correlations with installation torque.

- Ultimate capacity determined from load tests.

- Ultimate axial capacity of pile shaft.

- Ultimate axial capacity of pile shaft couplings.

- Sum of the ultimate axial capacity of helical bearing plates affixed to pile.

1810A.3.3.2 Allowable Lateral Load

Where required by the design, the lateral load capacity of a single deep foundation element or a group thereof shall be determined by an approved method of analysis or by lateral load tests in accordance with ASTM D3966 to not less than twice the proposed design working load. The resulting allowable lateral load shall not be more than one-half of the load that produces a gross lateral movement of 1 inch (25 mm) at the lower of the top of the foundation element and the ground surface, unless it can be shown that the predicted lateral movement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity. Group effects shall be evaluated where required by Section 1810A.2.5.

1810A.3.4 Subsiding Soils or Strata

Where deep foundation elements are installed through subsiding soils or other subsiding strata and derive support from underlying firmer materials, consideration shall be given to the downward frictional forces potentially imposed on the elements by the subsiding upper strata.

Where the influence of subsiding soils or strata is considered as imposing loads on the element, the allowable stresses specified in this chapter shall be permitted to be increased where satisfactory substantiating data are submitted.

1810A.3.5 Dimensions of Deep Foundation Elements

The dimensions of deep foundation elements shall be in accordance with Sections 1810A.3.5.1 through 1810A.3.5.3, as applicable.

1810A.3.5.1 Precast

The minimum lateral dimension of precast concrete deep foundation elements shall be 8 inches (203 mm). Corners of square elements shall be chamfered.

1810A.3.5.2 Cast-in-Place or Grouted-in-Place

Cast-in-place and grouted-in-place deep foundation elements shall satisfy the requirements of this section.

1810A.3.5.2.1 Cased

Cast-in-place or grouted-in-place deep foundation elements with a permanent casing shall have a nominal outside diameter of not less than 8 inches (203 mm).

1810A.3.5.2.2 Uncased

Cast-in-place or grouted-in-place deep foundation elements without a permanent casing shall have a specified diameter of not less than 12 inches (305 mm). The element length shall not exceed 30 times the specified diameter.

Exception: The length of the element is permitted to exceed 30 times the specified diameter, provided that the design and installation of the deep foundations are under the direct supervision of a registered design professional knowledgeable in the field of soil mechanics and deep foundations. The registered design professional shall submit a report to the building official stating that the elements were installed in compliance with the approved construction documents.

1810A.3.5.2.3 Micropiles

Micropiles shall have a nominal diameter of 12 inches (305 mm) or less. The minimum diameter set forth elsewhere in Section 1810A.3.5 shall not apply to micropiles.

1810A.3.5.3 Steel

Steel deep foundation elements shall satisfy the requirements of this section.

1810A.3.5.3.1 Structural Steel H-Piles

Sections of structural steel H-piles shall comply with the requirements for HP shapes in ASTM A6, or the following:

- The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall be not less than 80 percent of the depth of the section.

- The nominal depth in the direction of the web shall be not less than 8 inches (203 mm).

- Flanges and web shall have a minimum nominal thickness of 3/8 inch (9.5 mm).

For structures assigned to Seismic Design Category D, E or F, design and detailing of H-piles shall also conform to the requirements of AISC 341.

1810A.3.5.3.2 Fully Welded Steel Piles Fabricated From Plates

Sections of fully welded steel piles fabricated from plates shall comply with the following:

- The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall be not less than 80 percent of the depth of the section.

- The nominal depth in the direction of the web shall be not less than 8 inches (203 mm).

- Flanges and web shall have a minimum nominal thickness of 3/8 inch (9.5 mm).

1810A.3.5.3.3 Structural Steel Sheet Piling

Individual sections of structural steel sheet piling shall conform to the profile indicated by the manufacturer, and shall conform to the general requirements specified by ASTM A6.

Installation of sheet piling shall satisfy inspection, monitoring and observation requirements in Sections 1812A.6 and 1812A.7.

1810A.3.5.3.4 Steel Pipes and Tubes

Steel pipes and tubes used as deep foundation elements shall have a nominal outside diameter of not less than 8 inches (203 mm). Where steel pipes or tubes are driven open ended, they shall have not less than 0.34 square inch (219 mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 Nm) of pile hammer energy, or shall have the equivalent strength for steels having a yield strength greater than 35,000 psi (241 MPa) or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the pile section is appropriate for the selected hammer. Where a pipe or tube with wall thickness less than 0.179 inch (4.6 mm) is driven open ended, a suitable cutting shoe shall be provided. Concrete-filled steel pipes or tubes in structures assigned to Seismic Design Category C, D, E or F shall have a wall thickness of not less than 3/16 inch (5 mm). The pipe or tube casing for socketed drilled shafts shall have a nominal outside diameter of not less than 18 inches (457 mm), a wall thickness of not less than 3/8 inch (9.5 mm) and a suitable steel driving shoe welded to the bottom; the diameter of the rock socket shall be approximately equal to the inside diameter of the casing.

Exceptions:

- There is no minimum diameter for steel pipes or tubes used in micropiles.

- For mandrel-driven pipes or tubes, the minimum wall thickness shall be 1/10 inch (2.5 mm).

1810A.3.5.3.5 Helical Piles

Dimensions of the central shaft and the number, size and thickness of helical bearing plates shall be sufficient to support the design loads.

1810A.3.6 Splices

Splices shall be constructed so as to provide and maintain true alignment and position of the component parts of the deep foundation element during installation and subsequent thereto and shall be designed to resist the axial and shear forces and moments occurring at the location of the splice during driving and for design load combinations. Where deep foundation elements of the same type are being spliced, splices shall develop not less than 50 percent of the bending strength of the weaker section. Where deep foundation elements of different materials or different types are being spliced, splices shall develop the full compressive strength and not less than 50 percent of the tension and bending strength of the weaker section. Where structural steel cores are to be spliced, the ends shall be milled or ground to provide full contact and shall be full-depth welded.

Splices occurring in the upper 10 feet (3048 mm) of the embedded portion of an element shall be designed to resist at allowable stresses the moment and shear that would result from an assumed eccentricity of the axial load of 3 inches (76 mm), or the element shall be braced in accordance with Section 1810A.2.2 to other deep foundation elements that do not have splices in the upper 10 feet (3048 mm) of embedment.

1810A.3.6.1 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F splices of deep foundation elements shall develop the lesser of the following:

- The nominal strength of the deep foundation element.

- The axial and shear forces and moments from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

1810A.3.7 Top of Element Detailing at Cutoffs

Where a minimum length for reinforcement or the extent of closely spaced confinement reinforcement is specified at the top of a deep foundation element, provisions shall be made so that those specified lengths or extents are maintained after cutoff.

1810A.3.8 Precast Concrete Piles

Precast concrete piles shall be designed and detailed in accordance with ACI 318.

Exception: Where the axial load from seismic forces is amplified by the applicable overstrength factor, Ω0, the axial load limits in Section 18.13.5.10.6 of ACI 318 may be increased by two times.

1810A.3.9 Cast-in-Place Deep Foundations

Cast-in-place deep foundation elements shall be designed and detailed in accordance with Sections 1810A.3.9.1 through 1810A.3.9.6.

1810A.3.9.1 Design Cracking Moment

The design cracking moment (ϕMn) for a cast-in-place deep foundation element not enclosed by a structural steel pipe or tube shall be determined using the following equation:

Equation 18A-5

For SI:

where:

f 'c  = Specified compressive strength of concrete or grout, psi (MPa).

Sm = Elastic section modulus, neglecting reinforcement and casing, cubic inches (mm3).

1810A.3.9.2 Required Reinforcement

Where subject to uplift or where the required moment strength determined using the load combinations of ASCE 7, Section 2.3 exceeds the design cracking moment determined in accordance with Section 1810A.3.9.1, cast-in-place deep foundations not enclosed by a structural steel pipe or tube shall be reinforced. Where reinforcement is required, it shall be in compliance with Chapter 20 of ACI 318.

1810A.3.9.3 Placement of Reinforcement

Reinforcement where required shall be assembled and tied together and shall be placed in the deep foundation element as a unit before the reinforced portion of the element is filled with concrete.

Exceptions:

- Steel dowels embedded 5 feet (1524 mm) or less shall be permitted to be placed after concreting, while the concrete is still in a semifluid state.

- For deep foundation elements installed with a hollow-stem auger, tied reinforcement shall be placed after elements are concreted, while the concrete is still in a semifluid state. Longitudinal reinforcement without lateral ties shall be placed either through the hollow stem of the auger prior to concreting or after concreting, while the concrete is still in a semifluid state.

- For Group R-3 and U occupancies not exceeding two stories of light-frame construction, reinforcement is permitted to be placed after concreting, while the concrete is still in a semifluid state, and the concrete cover requirement is permitted to be reduced to 2 inches (51 mm), provided that the construction method can be demonstrated to the satisfaction of the building official.

1810A.3.9.4 Seismic Reinforcement

Where a structure is assigned to Seismic Design Category D, E or F, reinforcement shall be provided in accordance with Section 1810A.3.9.4.2.

Exceptions:

- Isolated deep foundation elements supporting posts of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where detailed so the element is not subject to lateral loads and the soil provides adequate lateral support in accordance with Section 1810A.2.1.

- Isolated deep foundation elements supporting posts and bracing from decks and patios appurtenant to Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where the lateral load, E, to the top of the element does not exceed 200 pounds (890 N) and the soil provides adequate lateral support in accordance with Section 1810A.2.1.

- Deep foundation elements supporting the concrete foundation wall of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than two No. 4 bars, without ties or spirals, where the design cracking moment determined in accordance with Section 1810A.3.9.1 exceeds the required moment strength determined using the load combinations with overstrength factor in Section 2.3.6 or 2.4.5 of ASCE 7 and the soil provides adequate lateral support in accordance with Section 1810A.2.1.

- Closed ties or spirals where required by Section 1810A.3.9.4.2 shall be permitted to be limited to the top 3 feet (914 mm) of deep foundation elements 10 feet (3048 mm) or less in depth supporting Group R-3 and U occupancies of Seismic Design Category D, not exceeding two stories of light-frame construction.

1810A.3.9.4.1 Seismic Reinforcement in Seismic Design Category C

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1810A.3.9.4.2 Seismic Reinforcement in Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, cast-in-place deep foundation elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis.

Not fewer than four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.005, shall be provided throughout the minimum reinforced length of the element as defined in this section starting at the top of the element. The minimum reinforced length of the element shall be taken as the greatest of the following:

- One-half of the element length.

- A distance of 10 feet (3048 mm).

- Three times the least element dimension.

- The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1810A.3.9.1 exceeds the required moment strength determined using the load combinations of ASCE 7, Section 2.3.

Transverse reinforcement shall consist of closed ties or spirals not smaller than No. 3 bars for elements with a least dimension up to 20 inches (508 mm), and No. 4 bars for larger elements. Throughout the remainder of the reinforced length outside the regions with transverse confinement reinforcement, as specified in Section 1810A.3.9.4.2.1 or 1810A.3.9.4.2.2, the spacing of transverse reinforcement shall not exceed the least of the following:

- 12 longitudinal bar diameters.

- One-half the least dimension of the element.

- 12 inches (305 mm).

Exceptions:

  - The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes.

  - A spiral-welded metal casing of a thickness not less than manufacturer's standard No. 14 gage (0.068 inch) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.

1810A.3.9.4.2.1 Site Classes A Through DE

For Site Class A, B, BC, C, CD, D or DE sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within three times the least element dimension at the bottom of the pile cap. A transverse spiral reinforcement ratio of not less than one-half of that required in Table 18.10.6.4(g) of ACI 318 shall be permitted for concrete deep foundation elements.

1810A.3.9.4.2.2 Site Classes E and F

For Site Class E or F sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within seven times the least element dimension at the bottom of the pile cap and within seven times the least element dimension at the interfaces of strata that are hard or stiff and strata that are liquefiable or are composed of soft- to medium-stiff clay.

1810A.3.9.5 Belled Drilled Shafts

Where drilled shafts are belled at the bottom, the edge thickness of the bell shall be not less than that required for the edge of footings. Where the sides of the bell slope at an angle less than 60 degrees (1 rad) from the horizontal, the effects of vertical shear shall be considered.

1810A.3.9.6 Socketed Drilled Shafts

Socketed drilled shafts shall have a permanent pipe or tube casing that extends down to bedrock and an uncased socket drilled into the bedrock, both filled with concrete. Socketed drilled shafts shall have reinforcement or a structural steel core for the length as indicated by an approved method of analysis.

The depth of the rock socket shall be sufficient to develop the full load-bearing capacity of the element with a minimum safety factor of two, but the depth shall be not less than the outside diameter of the pipe or tube casing. The design of the rock socket is permitted to be predicated on the sum of the allowable load-bearing pressure on the bottom of the socket plus bond along the sides of the socket.

Where a structural steel core is used, the gross cross-sectional area of the core shall not exceed 25 percent of the gross area of the drilled shaft.

1810A.3.10 Micropiles

Micropiles shall be designed and detailed in accordance with Sections 1810A.3.10.1 through 1810A.3.10.4.

1810A.3.10.1 Construction

Micropiles shall develop their load-carrying capacity by means of a bond zone in soil, bedrock or a combination of soil and bedrock. Micropiles shall be grouted and have either a steel pipe or tube or steel reinforcement at every section along the length. It shall be permitted to transition from deformed reinforcing bars to steel pipe or tube reinforcement by extending the bars into the pipe or tube section by not less than their development length in tension in accordance with ACI 318.

1810A.3.10.2 Materials

Reinforcement shall consist of deformed reinforcing bars in accordance with ASTM A615 Grade 60 or 75 or ASTM A722 Grade 150.

The steel pipe or tube shall have a minimum wall thickness of 3/16 inch (4.8 mm). Splices shall comply with Section 1810A.3.6. The steel pipe or tube shall have a minimum yield strength of 45,000 psi (310 MPa) and a minimum elongation of 15 percent as shown by mill certifications or two coupon test samples per 40,000 pounds (18 160 kg) of pipe or tube.

1810A.3.10.3 Reinforcement

For micropiles or portions thereof grouted inside a temporary or permanent casing or inside a hole drilled into bedrock or a hole drilled with grout, the steel pipe or tube or steel reinforcement shall be designed to carry not less than 40 percent of the design compression load. Micropiles or portions thereof grouted in an open hole in soil without temporary or permanent casing and without suitable means of verifying the hole diameter during grouting shall be designed to carry the entire compression load in the reinforcing steel. Where a steel pipe or tube is used for reinforcement, the portion of the grout enclosed within the pipe is permitted to be included in the determination of the allowable stress in the grout.

1810A.3.10.4 Seismic Requirements

For structures assigned to Seismic Design Category D, E or F, a permanent steel casing having a minimum thickness of 3/8 inch shall be provided from the top of the micropile down to a minimum of 120 percent of the point of zero curvature. Capacity of micropiles shall be determined in accordance with Section 1810A.3.3 by at least two project-specific preproduction tests for each soil profile, size and depth of micropile. At least two percent of all production piles shall be proof tested to the load determined in accordance with Section 1617A.1.15.

Steel casing length in soil shall be considered as unbonded and shall not be considered as contributing to friction. Casing shall provide confinement at least equivalent to hoop reinforcing required by ACI 318 Section 18.13.5.

Reinforcement shall have Class 1 corrosion protection in accordance with PTI Recommendations for Prestressed Rock and Soil Anchors. Steel casing design shall include at least 1/16-inch corrosion allowance.

Micropiles shall not be considered as carrying any horizontal loads.

1810A.3.11 Pile Caps

Pile caps shall conform with ACI 318 and this section. Pile caps shall be of reinforced concrete, and shall include all elements to which vertical deep foundation elements are connected, including grade beams and mats. The soil immediately below the pile cap shall not be considered as carrying any vertical load, with the exception of a combined pile raft. A combined pile raft foundation shall be an alternate system. The tops of vertical deep foundation elements shall be embedded not less than 3 inches (76 mm) into pile caps and the caps shall extend not less than 4 inches (102 mm) beyond the edges of the elements. The tops of elements shall be cut or chipped back to sound material before capping.

1810A.3.11.1 Seismic Design Categories C Through F

For structures assigned to Seismic Design Category C, D, E or F, concrete deep foundation elements shallbe connected to the pile cap in accordance with ACI318.

For resistance to uplift forces, anchorage of steel pipes, tubes or H-piles to the pile cap shall be made by means other than concrete bond to the bare steel section. Concrete-filled steel pipes or tubes shall have reinforcement of not less than 0.01 times the cross-sectional area of the concrete fill developed into the cap and extending into the fill a length equal to two times the required cap embedment, but not less than the development length in tension of the reinforcement.

1810A.3.11.2 Seismic Design Categories D Through F

For structures assigned to Seismic Design Category D, E or F, deep foundation element resistance to uplift forces or rotational restraint shall be provided by anchorage into the pile cap, designed considering the combined effect of axial forces due to uplift and bending moments due to fixity to the pile cap. Anchorage shall develop not less than 25 percent of the strength of the element in tension. Anchorage into the pile cap shall comply with the following:

- In the case of uplift, the anchorage shall be capable of developing the least of the following:

  - The nominal tensile strength of the longitudinal reinforcement in a concrete element.

  - The nominal tensile strength of a steel element.

  - The frictional force developed between the element and the soil multiplied by 1.3. [DSA-SS, DSA-SS/CC] Not permitted by DSA.

Exception: The anchorage is permitted to be designed to resist the axial tension force resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

- In the case of rotational restraint, the anchorage shall be designed to resist the axial and shear forces, and moments resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 or the anchorage shall be capable of developing the full axial, bending and shear nominal strength of the element.

- The connection between the pile cap and the steel H-piles or unfilled steel pipe piles in structures assigned to Seismic Design Category D, E or Fshall be designed for a tensile force of not less than 10 percent of the pile compression capacity.

Exception: Connection tensile capacity need not exceed the strength required to resist seismic load effects including overstrength of ASCE 7 Section 12.4.3 or 12.14.3.2.

Where the vertical lateral-force-resisting elements are columns, the pile cap flexural strengths shall exceed the column flexural strength. The connection between batter piles and pile caps shall be designed to resist the nominal strength of the pile acting as a short column. Batter piles and their connection shall be designed to resist forces and moments that result from the application of seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.

1810A.3.12 Grade Beams

Grade beams shall comply with the provisions of ACI 318.

Exception: Grade beams not subject to differential settlement exceeding one-fourth of the thresholds specified in ASCE 7 Table 12.13-3 and designed to resist the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 need not comply with ACI 318 Section 18.13.3.1.

1810A.3.13 Seismic Ties

Seismic ties shall comply with the provisions of ACI 318.

Exception: In Group R-3 and U occupancies of light-frame construction, deep foundation elements supporting foundation walls, isolated interior posts detailed so the element is not subject to lateral loads or exterior decks and patios are not subject to interconnection where the soils are of adequate stiffness, subject to the approval of the building official.

1810A.4 Installation

Deep foundations shall be installed in accordance with Section 1810A.4. Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section shall satisfy the applicable conditions of installation.

1810A.4.1 Structural Integrity

Deep foundation elements shall be installed in such a manner and sequence as to prevent distortion or damage that would adversely affect the structural integrity of adjacent structures or of foundation elements being installed or already in place and as to avoid compacting the surrounding soil to the extent that other foundation elements cannot be installed properly.

1810A.4.1.1 Compressive Strength of Precast Concrete Piles

A precast concrete pile shall not be driven before the concrete has attained a compressive strength of not less than 75 percent of the specified compressive strength (f 'c), but not less than the strength sufficient to withstand handling and driving forces.

1810A.4.1.2 Shafts in Unstable Soils

Where cast-in-place deep foundation elements are formed through unstable soils, the open hole shall be stabilized by a casing, slurry or other approved method prior to placing the concrete. Where the casing is withdrawn during concreting, the level of concrete shall be maintained above the bottom of the casing at a sufficient height to offset any hydrostatic or lateral soil pressure. Driven casings shall be mandrel driven their full length in contact with the surrounding soil.

1810A.4.1.3 Driving Near Uncased Concrete

Deep foundation elements shall not be driven within six element diameters center to center in granular soils or within one-half the element length in cohesive soils of an uncased element filled with concrete less than 48hours old unless approved by the building official. If driving near uncased concrete elements causes the concrete surface in any completed element to rise or drop significantly or bleed additional water, the completed element shall be replaced.

1810A.4.1.4 Driving Near Cased Concrete

Deep foundation elements shall not be driven within four and one-half average diameters of a cased element filled with concrete less than 24 hours old unless approved by the building official. Concrete shall not be placed in casings within heave range of driving.

1810A.4.1.5 Defective Timber Piles

Not permitted by DSA-SS, DSA-SS/CC or OSHPD.

1810A.4.2 Identification

Deep foundation materials shall be identified for conformity to the specified grade with this identity maintained continuously from the point of manufacture to the point of installation or shall be tested by an approved agency to determine conformity to the specified grade. The approved agency shall furnish an affidavit of compliance to the building official.

1810A.4.3 Location Plan

A plan showing the location and designation of deep foundation elements by an identification system shall be filed with the building official prior to installation of such elements. Detailed records for elements shall bear an identification corresponding to that shown on the plan.

1810A.4.4 Preexcavation

The use of jetting, augering or other methods of preexcavation shall be subject to the approval of the building official. Where permitted, preexcavation shall be carried out in the same manner as used for deep foundation elements subject to load tests and in such a manner that will not impair the carrying capacity of the elements already in place or damage adjacent structures. Element tips shall be advanced below the preexcavated depth until the required resistance or penetration is obtained.

1810A.4.5 Vibratory Driving

Vibratory drivers shall only be used to install deep foundation elements where the element load capacity is verified by load tests in accordance with Section 1810A.3.3.1.2.

Exceptions:

- The pile installation is completed by driving with an impact hammer in accordance with Section 1810A.3.3.1.1.

- The pile is to be used only for lateral resistance.

The installation of production elements shall be controlled according to power consumption, rate of penetration or other approved means that ensures element capacities equal or exceeding those of the test elements.

1810A.4.6 Heaved Elements

Deep foundation elements that have heaved during the driving of adjacent elements shall be redriven as necessary to develop the required capacity and penetration, or the capacity of the element shall be verified by load tests in accordance with Section 1810A.3.3.1.2.

1810A.4.7 Enlarged Base Cast-in-Place Elements

Enlarged bases for cast-in-place deep foundation elements formed by compacting concrete or by driving a precast base shall be formed in or driven into granular soils. Such elements shall be constructed in the same manner as successful prototype test elements driven for the project. Shafts extending through peat or other organic soil shall be encased in a permanent steel casing. Where a cased shaft is used, the shaft shall be adequately reinforced to resist column action or the annular space around the shaft shall be filled sufficiently to reestablish lateral support by the soil. Where heave occurs, the element shall be replaced unless it is demonstrated that the element is undamaged and capable of carrying twice its design load.

1810A.4.8 Hollow-Stem Augered, Cast-in-Place Elements

Where concrete or grout is placed by pumping through a hollow-stem auger, the auger shall be permitted to rotate in a clockwise direction during withdrawal. As the auger is withdrawn at a steady rate or in increments not to exceed 1 foot (305 mm), concreting or grouting pumping pressures shall be measured and maintained high enough at all times to offset hydrostatic and lateral earth pressures. Concrete or grout volumes shall be measured to ensure that the volume of concrete or grout placed in each element is equal to or greater than the theoretical volume of the hole created by the auger. Where the installation process of any element is interrupted or a loss of concreting or grouting pressure occurs, the element shall be redrilled to 5 feet (1524 mm) below the elevation of the tip of the auger when the installation was interrupted or concrete or grout pressure was lost and reformed. Augered cast-in-place elements shall not be installed within six diameters center to center of an element filled with concrete or grout less than 12 hours old, unless approved by the building official. If the concrete or grout level in any completed element drops due to installation of an adjacent element, the element shall be replaced.

1810A.4.9 Socketed Drilled Shafts

The rock socket and pipe or tube casing of socketed drilled shafts shall be thoroughly cleaned of foreign materials before filling with concrete. Steel cores shall be bedded in cement grout at the base of the rock socket.

1810A.4.10 Micropiles

Micropile deep foundation elements shall be permitted to be formed in holes advanced by rotary or percussive drilling methods, with or without casing. The elements shall be grouted with a fluid cement grout. The grout shall be pumped through a tremie pipe extending to the bottom of the element until grout of suitable quality returns at the top of the element. The following requirements apply to specific installation methods:

- For micropiles grouted inside a temporary casing, the reinforcing bars shall be inserted prior to withdrawal of the casing. The casing shall be withdrawn in a controlled manner with the grout level maintained at the top of the element to ensure that the grout completely fills the drill hole. During withdrawal of the casing, the grout level inside the casing shall be monitored to verify that the flow of grout inside the casing is not obstructed.

- For a micropile or portion thereof grouted in an open drill hole in soil without temporary casing, the minimum design diameter of the drill hole shall be verified by a suitable device during grouting.

- For micropiles designed for end bearing, a suitable means shall be employed to verify that the bearing surface is properly cleaned prior to grouting.

- Subsequent micropiles shall not be drilled near elements that have been grouted until the grout has had sufficient time to harden.

- Micropiles shall be grouted as soon as possible after drilling is completed.

- For micropiles designed with a full-length casing, the casing shall be pulled back to the top of the bond zone and reinserted or some other suitable means employed to ensure grout coverage outside the casing.

1810A.4.11 Helical Piles

Helical piles shall be installed to specified embedment depth and torsional resistance criteria as determined by a registered design professional. The torque applied during installation shall not exceed the manufacturer's rated maximum installation torque resistance of the helical pile.

1810A.4.12 Special Inspection

Special inspections in accordance with Sections 1705A.7 and 1705A.8 shall be provided for driven and cast-in-place deep foundation elements, respectively. Special inspections in accordance with Section 1705A.9 shall be provided for helical piles.

Section 1811A Prestressed Rock and Soil Foundation Anchors

1811A.1 General

The requirements of this section address the use of vertical rock and soil anchors in resisting seismic or wind overturning forces resulting in tension on shallow foundations.

1811A.2 Adoption

Except for the modifications as set forth in Sections 1811A.3 and 1811A.4, all prestressed rock and soil foundation anchors shall comply with PTI Recommendations for Prestressed Rock and Soil Anchors.

1811A.3 Geotechnical Requirements

Geotechnical report for the prestressed rock and soil foundation anchors shall address the following:

- Minimum diameter and minimum spacing for the anchors including consideration of group effects.

- Maximum unbonded length and minimum bonded length of the tendon.

- Maximum recommended anchor tension capacity based upon the soil or rock strength/grout bond and anchor depth/spacing.

- Allowable bond stress at the ground/grout interface and applicable factor of safety for ultimate bond stress.

- Anchor axial tension stiffness recommendations at the anticipated anchor axial tension displacements, when required for structural analysis.

- Minimum grout pressure for installation and post-grout pressure.

- Class I corrosion protection is required for all permanent and extended temporary anchors in service more than 2 years. A minimum of Class II corrosion protection is required for temporary anchors in service less than or equal to 2 years.

- Performance test shall be at a minimum of 1.6 times the design loads, but shall not exceed 80 percent of the specified minimum tensile strength of the tendons. There shall be a minimum of two preproduction test anchors. Preproduction test anchors shall be tested to ultimate load or maximum of 0.80 times the specified minimum tensile strength of the tendon. A creep test is required for all prestressed anchors with greater than 10 kips of lock-off prestressing load.

- Lock-off prestressing load requirements.

- Acceptable drilling methods.

- Geotechnical observation and monitoring requirements.

1811A.4 Structural Requirements

- Tendons shall be thread-bar anchors conforming to ASTM A722.

- The anchors shall be placed vertical.

- Design loads shall be based upon the load combinations in Section 2.4 of ASCE 7 and shall not exceed 60 percent of the specified minimum tensile strength of the tendons.

- Ultimate load shall be based upon Section 1617A.1.15 and shall not exceed 80 percent of the specified minimum tensile strength of the tendons.

- The anchor shall be designed to fail in grout bond to the soil or rock before pullout of the soil wedge by group effect.

- Foundation design shall incorporate the effect of lock-off loads.

- Design shall account for as-built locations of soil anchors considering all the acceptable construction tolerances.

- Design shall account for both short and long term deformation.

- Enforcement agency may require consideration of anchor deformation in evaluating deformation compatibility or building drift where it may be significant.

Section 1812A Earth Retaining Shoring

1812A.1 General

The requirements of this section shall apply to temporary and permanent earth retaining shoring using soldier piles and lagging with or without tie-back anchors in soil or rock, only when existing or new facilities are affected. Shoring used as construction means and methods only, which does not affect existing or new facilities, are not regulated by this section and shall satisfy the requirements of the authorities having jurisdiction.

Design, construction, testing and inspection shall satisfy the requirements of this code except as modified in Sections 1812A.2 through 1812A.8.

1812A.2 Duration

Shoring shall be considered temporary when elements of the shoring will be exposed to site conditions for a period of less than or equal to 2 years, and shall be considered permanent otherwise. Permanent shoring shall account for the increase in lateral soil pressure due to earthquake. At the end of the construction period, the existing and new structures shall not rely on the temporary shoring for support in any way. Wood components shall not be used for permanent shoring lasting more than 2 years. Wood components of the temporary shoring that may affect the performance of permanent structure shall be removed after the shoring is no longer required.

All components of the shoring shall have corrosion protection or preservative treatment for their expected duration. Wood components of the temporary shoring that will not be removed shall be treated in accordance with AWPA U1 (Commodity Specification A, Use Category 4B and compatible species in accordance with Section 5), and shall be identified in accordance with Section 2303.1.9.1.

1812A.3 Surcharge

Surcharge pressure due to footings, traffic or other sources shall be considered in design. If the footing surcharge is located within the semicircular distribution or bulb of earth pressure (when shoring is located close to a footings), lagging shall be designed for lateral earth pressure due to footing surcharge. Soil arching effects may be considered in the design of lagging. Underpinning of the footing may be used in lieu of designing the shoring and lagging for surcharge pressure. Alternatively, continuously contacting drilled pier shafts near the footings shall be permitted. The lateral surcharge design pressure shall be derived using Boussinesq equations modified for the distribution of stresses in an elastic medium due to a uniform, concentrated or line surface load as appropriate and soil arching effects.

1812A.4 Design and Testing:

Except for the modifications as set forth in Sections 1812A.4.1 through 1812A.4.3, all Prestressed Rock and Soil Tie-back Anchors shall comply with PTI Recommendations for Prestressed Rock and Soil Anchors.

1812A.4.1 Geotechnical Requirements:

The geotechnical report for the earth retaining shoring shall address the following:

- Minimum diameter and minimum spacing for the anchors including consideration of group effects.

- Maximum unbonded length and minimum bonded length of the tie-back anchors.

- Maximum recommended anchor tension capacity based upon the soil or rock strength/grout bond and anchor depth/spacing.

- Allowable bond stress at the ground/grout interface and applicable factor of safety for ultimate bond stress for the anchor. For permanent anchors, a minimum factor of safety of 2.0 shall be applied to ground soil interface as required by PTI Recommendations for Prestressed Rock and Soil Anchors Section 6.6.

- Minimum grout pressure for installation and post-grout pressure for the anchor. The presumptive post grout pressure of 300 psi may be used for all soil type.

- Class I corrosion protection is required for all permanent and extended temporary anchors in service more than 2 years. A minimum of Class II corrosion protection is required for temporary anchors in service less than or equal to 2 years.

- Performance test for the anchors shall be at a minimum of two (2) times the design loads and shall not exceed 80 percent of the specified minimum tensile strength of the anchor rod. A creep test is required for all prestressed anchors that are performance tested. All production anchors shall be tested at 150 percent of design loads and shall not be greater than 70 percent of the specified minimum tensile strength of the anchor rod.

- Earth pressure, surcharge pressure and the seismic increment of earth pressure loading, when applicable.

- Maximum recommended lateral deformation at the top of the soldier pile, at the tie-back anchor locations and the drilled pier concrete shafts at the lowest grade level.

- Allowable vertical soil bearing pressure friction resistance, and lateral passive soil resistance for the drilled pier concrete shafts and associated factors of safety for these allowable capacities.

- Soil-pier shaft/pile interaction assumptions and lateral soil stiffness to be used in design for drilled pier concrete shaft or pile lateral loads.

- Acceptable drilling methods.

- Geotechnical observation and monitoring recommendations.

1812A.4.2 Structural Requirements:

- Tendons shall be thread-bar anchors conforming to ASTM A722.

- Anchor design loads shall be based upon the load combinations in Section 2.4 of ASCE 7 and shall not exceed 60 percent of the specified minimum tensile strength of the tendons.

- The anchor shall be designed to fail in grout bond to the soil or rock before pullout of the soil wedge.

- Design of shoring system shall account for as-built locations of soil anchors considering all specified construction tolerances in Section 1812A.8.

- Design of shoring system shall account for both short and long-term deformation.

1812A.4.3 Testing of Tie-Back Anchors:

- The geotechnical engineer shall keep a record at job site of all test loads, total anchor movement, and report their accuracy.

- The shoring design engineer shall specify design loads for each anchor.

1812A.5 Construction

The construction procedure shall address the following:

- Holes drilled for piles/tie-back anchors shall be done without detrimental loss of ground, sloughing or caving of materials and without endangering previously installed shoring members or existing foundations.

- Drilling of earth anchor shafts for tie-backs shall occur when the drill bench reaches two to three feet below the level of the tie-back pockets.

- Casing or other methods shall be used where necessary to prevent loss of ground and collapse of the hole.

- The drill cuttings from earth anchor shaft shall be removed prior to anchor installation.

- Unless tremie methods are used, all water and loose materials shall be removed from the holes prior to installing piles/tie-backs.

- Tie-back anchor rods with attached centralizing devices shall be installed into the shaft or through the drill casing. Centralizing device shall not restrict movement of the grout.

- After lagging installation, voids between lagging and soil shall be backfilled immediately to the full height of lagging.

- The soldier piles shall be placed within specified tolerances in the drilled hole and braced against displacement during grouting. Shafts shall be filled with concrete up to the elevation shown on the construction documents. The remainder of the shaft shall be permitted to be filled with controlled low-strength material (CLSM) when permitted by the construction documents. Excavation for lagging shall not be started until concrete has achieved sufficient strength for all anticipated loads as determined by the shoring design engineer.

- Where boulders and/or cobbles have been identified in the geotechnical reports, contractor shall be prepared to address boulders and/or cobbles that may be encountered during the drilling of soldier piles and tie-back anchors.

- The grouting equipment shall produce grout free of lumps and indispensed cement. The grouting equipment shall be sized to enable the grout to be pumped in continuous operation. The mixer shall be capable of continuously agitating the grout.

- The quantity of grout and grout pressure shall be recorded. The grout pressure shall be controlled to prevent excessive heave in soils or fracturing rock formations.

- If post-grouting is required, post-grouting operation shall be performed after initial grout has set for 24 hours in the bond length only. Tie-backs shall be grouted over a sufficient length (anchor bond length) to transfer the maximum anchor force to the anchor grout.

- Testing of anchors in accordance with Section 1812A.4.1, Item 7 may be performed after post-grouting operations, provided grout has reached strength of 3,000 psi as required by PTI Recommendations for Prestressed Rock and Soil Anchors Section 6.11.

- Anchor rods shall be tensioned straight and true. Excavation directly below the anchors shall not continue before those anchors are tested.

- If a tie-back anchor initially fails the testing requirements, the anchor shall be permitted to be regrouted and retested. If anchor continues to fail, the followings steps shall be taken:

  - The contractor shall determine the cause of failure—variations of the soil conditions, installation methods, materials, etc.

  - The contractor shall propose a solution to remedy the problem. The proposed solution will need to be reviewed and approved by the geotechnical engineer, shoring design engineer and building official.

- After a satisfactory test, each anchor shall be locked-off in accordance with Section 8.4 of PTI Recommendations for Prestressed Rock and Soil Anchors.

1812A.6 Inspection, Survey Monitoring and Observation

- The shoring design engineer or his designee shall make periodic visits to the job site for the purpose of observing the installation of shoring system, testing of tie-back anchors and monitoring of survey.

- Testing, inspection and observation shall be in accordance with testing, inspection and observation requirements approved by the building official. The following activities and materials shall be tested, inspected or observed by the special inspector and geotechnical engineer:

  - Sampling and testing of concrete in soldier pile and tie-back anchor shafts.

  - Fabrication of tie-back anchor pockets on soldier beams

  - Installation and testing of tie-back anchors.

  - Survey monitoring of soldier pile and tie-back load cells.

  - Survey monitoring of existing buildings.

- A complete and accurate record of all soldier pile locations, depths, concrete strengths, tie-back locations and lengths, tie-back grout strength, quantity of concrete per pile, quantity of grout per tie-back and applied tie-back loads shall be maintained by the special inspector and geotechnical engineer. The shoring design engineer shall be notified of any unusual conditions encountered during installation.

- Calibration data for each test jack, pressure gauge and master pressure gauge shall be verified by the special inspector and geotechnical engineer. The calibration tests shall be performed by an independent testing laboratory and within 120 calendar days of the data submitted.

- Monitoring points shall be established at the top and at the anchor heads of selected soldier piles and at intermediate intervals as considered appropriate by the geotechnical engineer.

- Control points shall be established outside the area of influence of the shoring system to ensure the accuracy of the monitoring readings.

- The periodic basis of shoring monitoring, as a minimum, shall be as follows:

  - Initial monitoring shall be performed prior to any excavation.

  - Once excavation has begun, the periodic readings shall be taken weekly until excavation reaches the estimated subgrade elevation and the permanent foundation is complete.

  - If performance of the shoring is within established guidelines, shoring design engineer may permit the periodic readings to be bi-weekly. Once initiated, bi-weekly readings shall continue until the building slab at ground floor level is completed and capable of transmitting lateral loads to the permanent structure. Thereafter, readings can be monthly.

  - Where the building has been designed to resist lateral earth pressures, the periodic monitoring of the soldier piles and adjacent structure can be discontinued once the ground floor diaphragm and subterranean portion of the structure is capable of resisting lateral soil loads and approved by the shoring design engineer, geotechnical engineer and building official.

  - Additional readings shall be taken when requested by the special inspector, shoring design engineer, geotechnical engineer or building official.

- Monitoring reading shall be submitted to the shoring design engineer, engineer in responsible charge and building official within three working days after they are conducted. Monitoring readings shall be accurate to within 0.01 feet. Results are to be submitted in tabular form showing at least the initial date of monitoring and reading, current monitoring date and reading and difference between the two readings.

- If the total cumulative horizontal or vertical movement (from start of construction) of the existing buildings reaches 1/2 inch or soldier piles reaches 1 inch all excavation activities shall be suspended. The geotechnical and shoring design engineer shall determine the cause of movement, if any, and recommend corrective measures, if necessary, before excavation continues.

- If the total cumulative horizontal or vertical movement (from start of construction) of the existing buildings reaches 3/4 inch or soldier piles reaches 11/2 inches all excavation activities shall be suspended until the causes, if any, can be determined. Supplemental shoring shall be devised to eliminate further movement and the building official shall review and approve the supplemental shoring before excavation continues.

- Monitoring of tie-back anchor loads:

  - Load cells shall be installed at the tie-back heads adjacent to buildings at maximum interval of 50 feet, with a minimum of one load cells per wall.

  - Load cell readings shall be taken once a day during excavation and once a week during the remainder of construction.

  - Load cell readings shall be submitted to the geotechnical engineer, shoring design engineer, engineer in responsible charge and building official.

  - Load cell readings can be terminated once the temporary shoring no longer provides support for the buildings.

1812A.7 Monitoring of Existing Structures

- The contractor shall complete a written and photographic log of all existing structures within 100 ft or three times depth of shoring, prior to construction. A licensed surveyor shall document all existing substantial cracks in adjacent existing structures.

- The contractor shall document existing condition of wall cracks adjacent to shoring walls prior to start of construction.

- The contractor shall monitor existing walls for movement or cracking that may result from adjacent shoring.

- If excessive movement or visible cracking occurs, the contractor shall stop work and shore/reinforce excavation and contact the shoring design engineer and building official.

- Monitoring of the existing structure shall be at reasonable intervals as required by the registered design professional subject to approval of the building official. Monitoring shall be performed by a licensed surveyor and shall consist of vertical and lateral movement of the existing structures. Prior to starting shoring installation a preconstruction meeting shall take place between the contractor, shoring design engineer, surveyor, geotechnical engineer and building official to identify monitoring locations on existing buildings.

- If in the opinion of the building official or shoring design engineer, monitoring data indicate excessive movement or other distress, all excavation shall cease until the geotechnical engineer and shoring design engineer investigate the situation and make recommendations for remediation or continuing.

- All readings and measurements shall be submitted to the building official and shoring design engineer.

1812A.8 Tolerances

The following tolerances shall be specified on the construction documents.

- Soldier piles:

  - Horizontal and vertical construction tolerances for the soldier pile locations.

  - Soldier pile plumbness requirements (angle with vertical line).

- Tie-back anchors:

  - Allowable deviation of anchor projected angle from specified vertical and horizontal design projected angle.

  - Anchor clearance to the existing/new utilities and structures.

Section 1813A Vibro Stone Columns for Ground Improvement

1813A.1 General

This section shall apply to vibro stone columns (VSCs) for ground improvement using unbounded aggregate materials. Vibro stone column provisions in this section are intended to increase bearing capacity, reduce settlements and mitigate liquefaction for shallow foundations. These requirements shall not be used for grouted or bonded stone columns, ground improvement for deep foundation elements or changing site class. VSCs shall not be considered a deep foundation element. Ground improvement shall be installed under the entire building/structure footprint and not under isolated foundation elements only. Design, construction, testing and inspection shall satisfy the requirements of this code except as modified in Sections 1813A.2 through 1813A.5.

1813A.2 Geotechnical Report

The geotechnical report shall specify vibro stone column requirements to ensure uniformity in total and differential immediate settlement, long term settlement and earthquake induced settlement.

- Soil compaction shall be in accordance with California Geological Survey (CGS) Special Publication 117A (SP-117A): Guidelines for Evaluating and Mitigating Seismic Hazard in California.

- Area replacement ratio for the compaction elements and the basis of its determination shall be explained. Minimum factor of safety for soil compaction shall be in accordance with SP-117A.

- Depth of soil compaction elements and extent beyond the footprint of structures/foundation shall be defined. Extent beyond the foundation shall be half the depth of the VSCs with a minimum of 10 ft or an approved alternative.

- Minimum diameter and maximum spacing of soil compaction elements shall be specified. VSCs shall not be less than 2 feet in diameter, and center to center spacing shall not exceed 8 feet.

- The modulus of subgrade reactions for shallow foundations shall account for the presence of compaction elements.

- The modulus of subgrade reactions, long-term settlement and post-earthquake settlement shall be specified along with expected total and differential settlements for design.

- The acceptance criteria for Friction Cone and Piezocone Penetration Testing in accordance with ASTM D5778 complemented by the standard penetration test (SPT) in accordance with ASTM D1586, if necessary, to verify soil improvement shall be specified.

- The requirements for special inspection and observation by the geotechnical engineer shall be specified.

- A final verified report (FVR) documenting the installation of the ground improvement system and confirming that the ground improvement acceptance criteria have been met shall be prepared by the geotechnical engineer and submitted to the enforcement agency for review and approval.

1813A.3 Shallow Foundations

VSCs under the shallow foundation shall be located symmetrically around the centroid of the footing or load.

- There shall be a minimum of four stone columns under each isolated or continuous/combined footing or approved equivalent.

- The VSCs shall not be used to resist tension or overturning uplift from the shallow foundations.

- The foundation design for the shallow foundation shall consider the increased vertical stiffness of the VSCs as point supports for analysis, unless it is substantiated that the installation of the VSCs result in improvement of the surrounding soils such that the modulus of subgrade reaction, long term settlement and post-earthquake settlement can be considered uniform throughout.

1813A.4 Installation

VSCs shall be installed with vibratory probes. Vertical columns of compacted unbounded aggregate shall be formed through the soils to be improved by adding gravel near the tip of the vibrator and progressively raising and repenetrating the vibrator which will results in the gravel being pushed into the surrounding soil. Gravel aggregate for VSCs shall be well graded with a maximum size of 6 inches and not more than 10 percent smaller than 3/8 inch after compaction.

1813A.5 Construction Documents

Construction documents for VSCs, as a minimum, shall include the following:

- Size, depth and location of VSCs.

- Extent of soil improvements along with building/structure foundation outlines.

- Field verification requirements and acceptance criteria using CPT/SPT.

- The locations where CPT/SPT shall be performed.

- The testing, inspection and observation (TIO) program shall indicate the inspection and observation required for the VSCs.

- A note indicating foundation construction shall not commence until the final verified report specified in Section 1813A.2 Item 9 has been submitted to and approved by the enforcement agency.