Chapter 30 Elevators and Conveying Systems

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE
CHAPTER 30 — ELEVATORS AND CONVEYING SYSTEMS

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC- CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter | X |  |  |  |  |  |  | X | X |  | X | X | X | X | X | X |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) |  |  | X |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3001.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3001.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3001.4 |  |  | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3001.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3001.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3002.4a — 3002.4.6a |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3002.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3002.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3002.9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3002.10 — 3002.11 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.1.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.1.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.2.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.2.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.4 — 3003.4.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3005.1 — 3005.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3005.4.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3006.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3006.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3007.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3007.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3008.1.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3003.1.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3008.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3008.7.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3010 |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 30 contains the provisions that regulate vertical and horizontal transportation and material-handling systems installed in buildings. This chapter also provides several elements that protect occupants and assist emergency responders during fires.

ICC code development note: Code change proposals to sections preceded by the designation [F] and [BE] will be considered by a code development committee meeting during the 2024 (Group A) Code Development Cycle. All other code change proposals will be considered by a code development committee meeting during the 2025 (Group B) Code Development Cycle.

Section 3001 General

3001.1 Scope

This chapter governs the design, construction, installation, alteration and repair of elevators and conveying systems and their components.

3001.2 Elevator Emergency Communication Systems

An elevator emergency two-way communication system that includes both visual and audible communication modes complying with the requirements in California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders, shall be provided in each elevator car. The system shall provide a means to enable authorized personnel to verify:

- The presence of someone in the car.

- That the person(s) is trapped.

Once an entrapment is verified, the system shall enable authorized personnel to:

- Determine if assistance is needed.

- Communicate when help is on the way.

- Communicate when help arrives on site.

3001.3 Referenced Standards

The design, construction, installation, alteration, repair and maintenance of elevators and conveying systems and their components shall conform to California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders, and the applicable standard specified in Table 3001.3 and Section 3001.6.

TABLE 3001.3—ELEVATORS AND CONVEYING SYSTEMS AND COMPONENTS

| TYPE | STANDARD |
| --- | --- |
| Automotive lifts | ALI ALCTV |
| Belt manlifts | ASME A90.1 |
| Conveyors and related equipment | ASME B20.1 |
| Elevators, escalators, dumbwaiters, moving walks, material lifts | ASME A17.1/CSA B44, ASME A17.7/CSA B44.7 |
| Industrial scissor lifts | ANSI MH29.1 |
| Platform lifts, stairway chairlifts, wheelchair lifts | ASME A18.1 |

[BE] 3001.4 Accessibility

Diagram

Passenger elevators and platform (wheelchair) lifts required to be accessible or to serve as part of an accessible means of egress shall comply with Sections 1009 and either Chapter 11A for applications listed in Section 1.8.2.1.2 regulated by the Department of Housing and Community Development or Chapter 11B for applications listed in Section 1.9.1 regulated by the Division of the State Architect—Access Compliance.

UpCodes Diagram (1)

Primary

Elevator Sill Depression: Example

3001.5 Change in Use

A change in use of an elevator from freight to passenger, passenger to freight, or from one freight class to another freight class shall comply with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3001.6 Structural Design

All interior and exterior elevators, escalators and other conveying systems and their components shall comply with all applicable design loading criteria in Chapter 16, including wind, flood and seismic loads established in Sections 1609, 1612 and 1613.

3001.7 Elevators Utilized to Transport Hazardous Materials

Elevators utilized to transport hazardous materials shall also comply with the California Fire Code Sections 5003.10.2.2, 5003.10.4 through 5003.10.7.

Section 3002 Hoistway Enclosures

3002.1 Hoistway Protection

A hoistway for elevators, dumbwaiters and other vertical-access devices shall comply with Sections 712 and 713. Where the hoistway is required to be enclosed, it shall be constructed as a shaft enclosure in accordance with Section 713.

3002.1.1 Opening Protectives

Openings in fire-resistance-rated hoistway enclosures shall be protected as required in Chapter 7.

Exception: The elevator car doors and the associated hoistway doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I Emergency Recall Operation.

3002.1.2 Hardware

Hardware on elevator hoistway doors shall be of an approved type installed as tested, except that approved interlocks, mechanical locks and electric contacts, door and gate electric contacts and door-operating mechanisms shall be exempt from the fire test requirements.

3002.2 Number of Elevator Cars in a Hoistway

Where four or more elevator cars serve all or the same portion of a building, the elevators shall be located in not fewer than two separate fire-resistance-rated hoistways. Not more than four elevator cars shall be located in any single fire-resistance-rated hoistway enclosure.

3002.3 Emergency Signs

A pictorial sign of a standardized design shall be posted adjacent to each elevator call station on all floors instructing occupants to use the exit stairways and not to use the elevators in case of fire. Where elevators are not a component of the accessible means of egress, the sign shall read: IN CASE OF FIRE, ELEVATORS ARE OUT OF SERVICE. USE EXIT. Where the elevator is a component of the accessible means of egress, a sign complying with Section 1009.11 shall be provided.

Exception: The emergency sign shall not be required for elevators that are used for occupant self-evacuation in accordance with Section 3008.

3002.4 Elevator Car to Accommodate Ambulance Stretcher

Diagram

Where elevators are provided in buildings four or more stories above, or four or more stories below, grade plane, not fewer than one elevator shall be provided for fire department emergency access to all floors. The elevator car shall be of such a size and arrangement to accommodate an ambulance stretcher 24 inches by 84 inches (610 mm by 2134 mm) with not less than 5-inch (127 mm) radius corners, in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall be not less than 3 inches (76 mm) in height and shall be placed inside on both sides of the hoistway door frame.

The following California sections replace the corresponding model code section for applications specified in section 1.11 for the Office of the State Fire Marshal.

UpCodes Diagram (1)

Primary

Elevator Car Dimensions

3002.4a General Stretcher Requirements

All buildings and structures with one or more passenger service elevators shall be provided with not less than one medical emergency service elevator to all landings meeting the provisions of Section 3002.4a. The medical emergency service elevator(s) shall be identified in the construction documents specified in Section 107 or the California Administrative Code.

Exceptions:

- Elevators in structures used only by maintenance and operating personnel.

- Elevators in jails and penal institutions.

- Elevators in buildings or structures where each landing is at ground level or is accessible at grade level or by a ramp.

- Elevator(s) in two-story buildings or structures equipped with stairs of a configuration that will accommodate the carrying of the gurney or stretcher as permitted by the local jurisdictional authority.

- Elevators in buildings or structures less than four stories in height for which the local jurisdictional authority has granted an exception in the form of a written document.

3002.4.1a Gurney Size

The medical emergency service elevator shall accommodate the loading and transport of two emergency personnel, each requiring a minimum clear 21-inch (533 mm) diameter circular area and an ambulance gurney or stretcher [minimum size 24 inches by 84 inches (610 mm by 2134 mm) with not less than 5-inch (127 mm) radius corners] in the horizontal, open position.

3002.4.2a Hoistway Doors

The hoistway landing openings shall be provided with power-operated doors.

3002.4.3a Elevator Recall

The elevator(s) designated the medical emergency elevator shall be equipped with a key switch to recall the elevator nonstop to the main floor. For the purpose of this section, elevators in compliance with Section 3003.2 shall be acceptable.

3002.4.4a Designation

Medical emergency elevators shall be identified by the international symbol (Star of Life) for emergency medical services.

3002.4.5a Symbol Size

The symbol shall not be less than 3 inches (76 mm) in size.

3002.4.6a Symbol Location

A symbol shall be permanently attached to each side of the hoistway door frame on the portion of the frame at right angles to the hallway or landing area. Each symbol shall be not less than 78 inches (1981 mm) and not more than 84 inches (2134 mm) above the floor level at the threshold.

3002.5 Emergency Doors

Where an elevator is installed in a single blind hoistway or on the outside of a building, there shall be installed in the blind portion of the hoistway or blank face of the building, an emergency door shall be in conformance with the California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3002.6 Prohibited Doors or Other Devices

Doors or other devices, other than the elevator car door and the associated elevator hoistway doors, shall be prohibited at the point of access to an elevator car unless such doors or other devices are readily openable from inside the car without a key, tool, special knowledge or effort.

3002.6.1 Prohibited Hoistway Access Doors and Panels

The following types of access doors and panels are prohibited in accordance with the California Code Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders:

- Access panels or doors to working platforms in the line of movement of the car counterweight in the hoistway.

- Access panels or doors in the hoistway for access to car or hoistway transparent enclosures.

3002.7 Common Enclosure With Stairway

Elevators shall not be in a common shaft enclosure with a stairway.

Exception: Elevators within open parking garages need not be separated from stairway enclosures.

3002.8 Glass in Elevator Enclosures

Glass in elevator enclosures shall comply with Section 2409.2.

3002.9 Plumbing and Mechanical Systems

Plumbing and mechanical systems shall not be located in an elevator hoistway enclosure unless permitted by California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

Exception: Floor drains and sumps and sump pumps shall be permitted at the base of the hoistway enclosure provided that they are indirectly connected to the plumbing system.

3002.10 Photoelectric Tube Bypass Switch

3002.10.1

Elevators equipped with photoelectric tube devices which control the closing of automatic, power-operated car or hoistway doors, or both, shall have a switch in the car which, when actuated, will render the photoelectric tube device ineffective.

3002.10.2

The switch shall be constant-pressure type, requiring not less than 10 pounds (44.5N) or more than 15 pounds (66.7 N) pressure to actuate.

3002.10.3

The switch shall be located not less than 6 feet (1829 mm) or more than 6 feet 6 inches (1981 mm) above the car floor and shall be located in or adjacent to the operating panel.

3002.10.4

The switch shall be clearly labeled TO BE USED IN CASE OF FIRE ONLY.

3002.10.5

Switches shall be kept in working order or be removed when existing installations are arranged to comply with Section 3002.10.5, Exception 1 or 2.

Exceptions:

- Elevators installed and maintained in compliance with Section 3003.

- Where alternate means acceptable to the fire authority having jurisdiction are provided that will ensure the doors can close under adverse smoke conditions.

3002.11 Pit Access Door

Where separate pit access door(s) are required for access to pit(s) located below the bottom hoistway door landing, permanent stairway access shall be provided to the access door.

Section 3003 Emergency Operations

Diagram

UpCodes Diagram (1)

High Rise: Emergency Systems

[F] 3003.1 Standby Power

In buildings and structures where standby power is required or furnished to operate an elevator, the operation shall be in accordance with Section 1203 of the California Fire Code and Sections 3003.1.1 through 3003.1.5 of this code.

[F] 3003.1.1 Manual Transfer

Standby power shall be manually transferable to all elevators in each bank.

[F] 3003.1.2 One Elevator

Where only one elevator is installed, the elevator shall automatically transfer to standby power within 60 seconds after failure of normal power.

[F] 3003.1.3 Two or More Elevators

Where two or more elevators are controlled by a common operating system, all elevators shall automatically transfer to standby power within 60 seconds after failure of normal power where the standby power source is of sufficient capacity to operate all elevators at the same time. Where the standby power source is not of sufficient capacity to operate all elevators at the same time, all elevators shall transfer to standby power in sequence, return to the designated landing and disconnect from the standby power source. After all elevators have been returned to the designated level, not less than one elevator shall remain operable from the standby power source.

[F] 3003.1.4 Temperature and Humidity Control

Where standby power is connected to elevators, the machine room machine space, control room and control space ventilation or air conditioning system shall be connected to the standby power source.

3003.1.5 Emergency Hoistway Venting

Where standby power is connected to elevators, the emergency hoistway ventilation system, if required, shall be connected to the standby power source.

[F] 3003.2 Firefighters' Emergency Operation

Elevators shall be provided with Phase I emergency recall operation and Phase II emergency in-car operation in accordance with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3003.2.1 Floor Numbers

Elevator hoistways shall have a floor number not less than 4 inches (102 mm) in height, placed on the walls and/or doors of the hoistway at intervals such that a person in a stalled elevator, upon opening the car door, can determine the floor position.

3003.2.1.1 Fire Signs

All automatic elevators shall have not less than one sign at each landing printed on a contrasting background in letters not less than 1/2 inch (12.7 mm) high to read: IN CASE OF FIRE USE STAIRWAY FOR EXIT. DO NOT USE ELEVATOR.

3003.2.1.2 Call and Car Operation Buttons

Automatic passenger elevators shall have call and car operation buttons within 60 inches (1524 mm) of the floor. Emergency telephones shall also be within 60 inches (1524 mm) of the floor.

[F] 3003.3 Standardized Fire Service Elevator Keys

All elevators shall be equipped to operate with a standardized fire service elevator key in accordance with the California Fire Code.

3003.4 Emergency Hoistway Venting

Elevator hoistways containing the driving machine shall be provided with a means for venting smoke and hot gases to the outer air in case of fire.

3003.4.1 Location of Vents

Vents shall be located at the top of the hoistway and shall open either directly to the outer air or through noncombustible ducts to the outer air.

3003.4.2 Area of Vents

Except as provided for in Section 3003.1.4.4, the area of the vents shall be not less than 31/2 percent of the area of the hoistway nor less than 3 square feet (0.28 m2) for each elevator car.

3003.4.3 Operation of Vents

Vent openings shall automatically open upon detection of smoke in the elevator hoistway and upon activation of a manual override control. The manual override control shall be capable of opening and closing the vents and shall be located in an approved location. Smoke detectors provided in elevator hoistways to activate the hoistway ventilation system, shall also be required to activate the elevator Phase I emergency recall operation function in accordance with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3003.4.4 Reduced Vent Area

Where mechanical ventilation conforming to the California Mechanical Code is provided, a reduction in the required vent area is allowed provided that all of the following conditions are met:

- The vents required by Section 3003.1.4.1 of the California Building Code do not have outside exposure.

- The hoistway does not extend to the top of the building.

- The hoistway exhaust fan is automatically reactivated by thermostatic means.

- Equivalent venting of the hoistway is accomplished.

Section 3004 Conveying Systems

3004.1 General

Escalators, moving walks, conveyors, personnel hoists and material hoists shall comply with the provisions of Sections 3004.2 through 3004.4.

3004.2 Escalators and Moving Walks

Escalators and moving walks shall be constructed of approved noncombustible and fire-retardant materials. This requirement shall not apply to electrical equipment, wiring, wheels, handrails and the use of 1/28-inch (0.9 mm) wood veneers on balustrades backed up with noncombustible materials.

3004.2.1 Enclosure

Escalator floor openings shall be enclosed with shaft enclosures complying with Section 713.

3004.2.2 Escalators

Diagram

Where provided in below-grade transportation stations, escalators shall have a clear width of not less than 32 inches (815 mm).

UpCodes Diagram (1)

Escalator Openings (New Const.)

3004.3 Conveyors

Conveyors and conveying systems shall comply with ASME B20.1.

3004.3.1 Enclosure

Conveyors and related equipment connecting successive floors or levels shall be enclosed with shaft enclosures complying with Section 713.

3004.3.2 Conveyor Safeties

Power-operated conveyors, belts and other material-moving devices shall be equipped with automatic limit switches that will shut off the power in an emergency and automatically stop all operation of the device.

3004.4 Personnel and Material Hoists

Personnel and material hoists shall be designed utilizing an approved method that accounts for the conditions imposed during the intended operation of the hoist device. The design shall include, but is not limited to, anticipated loads, structural stability, impact, vibration, stresses and seismic restraint. The design shall account for the construction, installation, operation and inspection of the hoist tower, car, machinery and control equipment, guide members and hoisting mechanism. Additionally, the design of personnel hoists shall include provisions for field testing and maintenance that will demonstrate that the hoist device functions in accordance with the design. Field tests shall be conducted upon the completion of an installation or following a major alteration of a personnel hoist.

Section 3005 Machine Rooms

3005.1 Access

A permanent and approved means of access shall be provided to elevator machine rooms, control rooms, control spaces and machinery spaces.

3005.2 Temperature and Humidity Control

Elevator machine rooms, machinery spaces that contain the driving machine, and control rooms or spaces that contain the operation or motion controller for elevator operation shall be provided with an independent ventilation or air-conditioning system to protect against the overheating of the electrical equipment. The system shall maintain the temperature and humidity be capable of maintaining temperatures within the range established by the manufacturer of the elevator equipment.

3005.3 Pressurization

Diagram

The elevator machine room, control rooms or control space with openings into a pressurized elevator hoistway shall be pressurized upon activation of a heat or smoke detector located in the elevator machine room, control room or control space.

UpCodes Diagram (1)

Recessed Mounting of Detector

3005.4 Machine Rooms, Control Rooms, Machinery Spaces, and Control Spaces

Assembly

The following rooms and spaces shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both:

- Machine rooms.

- Control rooms.

- Control spaces.

- Machinery spaces outside of the hoistway enclosure.

The fire-resistance rating shall be not less than the required rating of the hoistway enclosure served by the machinery. Openings in the fire barriers shall be protected with assemblies having a fire protection rating not less than that required for the hoistway enclosure doors.

Exceptions:

- For other than fire service access elevators and occupant evacuation elevators, where machine rooms, machinery spaces, control rooms and control spaces do not abut and do not have openings to the hoistway enclosure they serve, the fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, shall be permitted to be reduced to a 1-hour fire-resistance rating.

- For other than fire service access elevators and occupant evacuation elevators, in buildings four stories or less above grade plane where machine room, machinery spaces, control rooms and control spaces do not abut and do not have openings to the hoistway enclosure they serve, the machine room, machinery spaces, control rooms and control spaces are not required to be fire-resistance rated.

Assemblies (4)

14-1.1: 1hr, Wood Joist

21-1.1: 1hr, Wood Joist

13-1.1: 1hr Steel Studs

13-1.2: 2hr, Steel Studs

Building products (7)

FF109-200 1 Hour Fire Rated LED Downlight Cover

Tenmat

FF109-250 1 Hour Fire Rated LED Downlight Cover

Tenmat

FF109-300 UL Fire Rated Recessed Light Cover

Tenmat

FF109-350 Fire Rated Light Cover

Tenmat

FF109-FRSC 1 Hour Fire Rated Speaker Cover

Tenmat

FF130 - 2x2 Fire Rated Troffer Cover

Tenmat

FF130 - 2x4 Fire Rated Troffer Cover

Tenmat

3005.4.1 Automatic Sprinkler System

Automatic sprinklers shall not be required to be installed in the elevator hoistway, elevator machine room, elevator machinery space, elevator control space or elevator control room where the following is met:

The elevator machine room, elevator machinery space, elevator control space or elevator control room shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall not be less than the required rating of the hoistway enclosure served by the machinery. Openings in the fire barriers shall be protected with assemblies having a fire protection rating not less than that required for the hoistway enclosure doors. The exceptions to Section 3005.4 shall not apply.

3005.5 Shunt Trip

Where elevator hoistways, elevator machine rooms, control rooms and control spaces containing elevator control equipment are protected with automatic sprinklers, a means installed in accordance with Section 21.4 of NFPA 72 shall be provided to automatically disconnect the main line power supply to the affected elevator prior to the application of water. This means shall not be self-resetting. The activation of automatic sprinklers outside the hoistway, machine room, machinery space, control room or control space shall not disconnect the main line power supply.

3005.6 Plumbing Systems

Plumbing systems shall not be located in elevator equipment rooms.

Section 3006 Elevator Lobbies and Hoistway Opening Protection

3006.1 General

Enclosed elevator lobbies and elevator hoistway door protection shall be provided in accordance with the following:

- Where elevator hoistway door protection is required by Section 3006.2, such protection shall be provided in accordance with Section 3006.3.

- Where enclosed elevator lobbies are required for underground buildings, such lobbies shall comply with Section 405.4.3.

- Where an area of refuge is required and an enclosed elevator lobby is provided to serve as an area of refuge, the enclosed elevator lobby shall comply with Section 1009.6.4.

- Where fire service access elevators are provided, enclosed elevator lobbies shall comply with Section 3007.6.

- Where occupant evacuation elevators are provided, enclosed elevator lobbies shall comply with Section 3008.6.

3006.2 Elevator Hoistway Door Protection Required

Elevator hoistway doors shall be protected in accordance with Section 3006.3 where an elevator hoistway connects more than two stories in any state institution or other state-owned or specified state occupied building regulated by the Office of the State Fire Marshal, and more than three stories for all other buildings. Hoistway opening protection is required to be enclosed within a shaft enclosure in accordance with Section 712.1.1 and any of the following conditions apply:

- The building is not protected throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.

- Group A occupancies.

- Group E occupancies.

- Group H occupancies.

- Group I occupancies.

- Group L occupancies.

- Group R-1, R-2, R-2.1 and R-2.2 occupancies.

- High-rise buildings.

- The elevator hoistway door is located in the wall of a corridor required to be fire-resistance rated in accordance with Section 1020.1.

See Section 403.6 for additional requirements for high-rise buildings.

Exceptions:

- Protection of elevator hoistway doors is not required where the elevator serves only open parking garages in accordance with Section 406.5.

- Protection of elevator hoistway doors is not required at the levels of exit discharge, provided that the levels of exit discharge is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.

- Protection of elevator hoistway doors is not required on levels where the elevator hoistway doors open to the exterior.

3006.2.1 Rated Corridors

Where corridors are required to be fire-resistance rated in accordance with Section 1020.2, elevator hoistway openings shall be protected in accordance with Section 3006.3.

3006.3 Elevator Hoistway Door Protection

Where Section 3006.2 requires protection of the elevator hoistway doors, the protection shall be provided by one of the following:

- An enclosed elevator lobby shall be provided at each floor to separate the elevator hoistway doors from each floor with fire partitions in accordance with Section 708. In addition, doors protecting openings in the fire partitions shall comply with Section 716.2.2.1. Penetrations of the fire partitions by ducts and air transfer openings shall be protected as required for corridors in accordance with Section 717.5.4.1.

- An enclosed elevator lobby shall be provided at each floor to separate the elevator hoistway doors from each floor by smoke partitions in accordance with Section 710. In addition, doors protecting openings in the smoke partitions shall comply with Sections 710.5.2.2, 710.5.2.3 and 716.2.6.1. Penetrations of the smoke partitions by ducts and air transfer openings shall be protected as required for corridors in accordance with Section 717.5.4.1.

- Additional doors or other devices shall be provided at each elevator hoistway door in accordance with Section 3002.6. Such doors or other devices shall comply with the smoke and draft control door assembly requirements in Section 716.2.2.1.1 when tested in accordance with UL 1784 without an artificial bottom seal.

- [SFM] When approved, in other than Group I-2 occupancies elevator hoistway shall be pressurized in accordance with Section 909.21.

- A smoke-protective curtain assembly for hoistways shall be provided at each elevator hoistway door opening in accordance with Section 3002.6. Such curtain assemblies shall comply with the smoke and draft control requirements in Section 716.2.2.1.1 when tested in accordance with UL 1784 without an artificial bottom seal. Such curtain assemblies shall be equipped with a control unit listed to UL 864. Such curtain assemblies shall comply with Section 2.11.6.3 California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders. Installation and maintenance shall be in accordance with NFPA 105.

- [SFM] Enclosed elevator lobbies are not required where the hoistway door has a fire-protection rating as required by Section 707.6 and the hoistway door opening is also protected by a listed and labeled smoke containment system complying with ICC ES AC 77.

3006.4 Means of Egress

Elevator lobbies shall be provided with not less than one means of egress complying with Chapter 10 and other provisions in this code. Egress through an enclosed elevator lobby shall be permitted in accordance with Item 1 of Section 1016.2. Electrically locked exit access doors providing egress from elevator lobbies shall be permitted in accordance with Section 1010.2.14.

Section 3007 Fire Service Access Elevator

Diagram

UpCodes Diagrams (3)

Smoke Barriers: Elevator Enclosures

Hoistway Water Protection

Fire Service Access Elev. Lobby

3007.1 General

Where required by Section 403.6.1, every floor above and including the lowest level of fire department vehicle access of the building shall be served by fire service access elevators complying with Sections 3007.1 through 3007.9. Except as modified in this section, fire service access elevators shall be installed in accordance with this chapter and California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

Exceptions:

- Below grade parking garage floors shall not be required to be served by fire service access elevators.

- The elevator shall not be required to serve the top floor of a building where that floor is utilized only for equipment for building systems.

3007.2 Automatic Sprinkler System

The building shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3007.2.1.

3007.2.1 Prohibited Locations

Automatic sprinklers shall not be installed in machine rooms, elevator machinery spaces, control rooms, control spaces and elevator hoistways of fire service access elevators.

3007.2.2 Automatic Sprinkler System Monitoring

The automatic sprinkler system shall have a sprinkler control valve supervisory switch and water-flow-initiating device provided for each floor that is monitored by the building's fire alarm system.

3007.3 Water Protection

Diagram

Water from the operation of an automatic sprinkler system outside the enclosed lobby shall be prevented from infiltrating into the hoistway enclosure in accordance with an approved method.

UpCodes Diagram (1)

Primary

Hoistway Water Protection

3007.4 Shunt Trip

Means for elevator shutdown in accordance with Section 3005.5 shall not be installed on elevator systems used for fire service access elevators.

3007.5 Hoistway Enclosures

The fire service access elevator hoistway shall be located in a shaft enclosure complying with Section 713.

3007.5.1 Structural Integrity of Hoistway Enclosures

The fire service access elevator hoistway enclosure shall comply with Sections 403.2.2.1 through 403.2.2.4.

3007.5.2 Hoistway Lighting

When firefighters' emergency operation is active, the entire height of the hoistway shall be illuminated at not less than 1 footcandle (11 lux) as measured from the top of the car of each fire service access elevator.

3007.6 Fire Service Access Elevator Lobby

The fire service access elevator shall open into an enclosed fire service access elevator lobby in accordance with Sections 3007.6.1 through 3007.6.5. Egress is permitted through the enclosed elevator lobby in accordance with Item 1 of Section 1016.2.

Exceptions:

- Where a fire service access elevator has two entrances onto a floor, the second entrance shall be permitted to be protected in accordance with Section 3006.3.

- A fire service access elevator lobby is not required to be provided at an occupiable roof.

3007.6.1 Access to Smokeproof Enclosure

The enclosed fire service access elevator lobby shall have direct access from the enclosed elevator lobby to a smokeproof enclosure complying with Section 909.20.

Exception: Access to a smokeproof enclosure shall be permitted to be through a protected path of travel that has a level of fire protection not less than the elevator lobby enclosure. The protected path shall be separated from the enclosed elevator lobby through an opening protected by a smoke and draft control assembly in accordance Section 716.2.2.1.

3007.6.2 Elevator Lobby Separation

Diagram

The fire service access elevator lobby shall be separated from each floor with a smoke barrier in accordance with Section 709, except that lobby doorways shall comply with Section 3007.6.3.

Exception: Fire service access elevator lobbies are not required to be separated at the levels of exit discharge.

UpCodes Diagrams (2)

Door Fire Ratings in Protective Wall Assemblies

Smoke Barriers: Elevator Enclosures

Building products (3)

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

3007.6.3 Elevator Lobby Doorways

Other than doors to the elevator control room or elevator control space, each door in the smoke barrier shall be provided with a 3/4-hour fire door assembly complying with Section 716. Such a fire door assembly shall comply with the smoke and draft control door assembly requirements of Section 716.2.2.1.1 and be tested in accordance with UL 1784 without an artificial bottom seal.

Building products (4)

GPX® Ballistic

SaftiFirst

SuperClear® 45-HS

SaftiFirst

SuperClear® 45-HS-LI

SaftiFirst

SuperLite® X-45/60/90

SaftiFirst

3007.6.4 Lobby Size

Diagram

Regardless of the number of fire service access elevators served by the same elevator lobby, the enclosed fire service access elevator lobby shall be not less than 150 square feet (14 m2) in an area with a dimension of not less than 8 feet (2440 mm).

UpCodes Diagram (1)

Primary

Fire Service Access Elev. Lobby

3007.6.5 Fire Service Access Elevator Symbol

A pictorial symbol of a standardized design designating which elevators are fire service access elevators shall be installed on each side of the hoistway door frame on the portion of the frame at right angles to the fire service access elevator lobby. The fire service access elevator symbol shall be designed as shown in Figure 3007.6.5 and shall comply with the following:

- The fire service access elevator symbol shall be not less than 3 inches (76 mm) in height.

- The helmet shall contrast with the background, with either a light helmet on a dark background or a dark helmet on a light background.

- The vertical center line of the fire service access elevator symbol shall be centered on the hoistway door frame. Each symbol shall be not less than 78 inches (1981 mm), and not more than 84 inches (2134 mm) above the finished floor at the threshold.

FIGURE 3007.6.5—FIRE SERVICE ACCESS ELEVATOR SYMBOL

For SI: 1 inch = 25.4 mm.

3007.7 Elevator System Monitoring

The fire service access elevator shall be continuously monitored at the fire command center by a standard emergency service interface system meeting the requirements of NFPA 72.

3007.8 Electrical Power

The following features serving each fire service access elevator shall be supplied by both normal power and Type 60/Class 2/Level 1 standby power:

- Elevator equipment.

- Elevator hoistway lighting.

- Ventilation and cooling equipment for elevator machine rooms, control rooms, machine spaces and control spaces.

- Elevator car lighting.

3007.8.1 Protection of Wiring or Cables

Assembly

Wires or cables that are located outside of the elevator hoistway and machine room and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to fire service access elevators shall be protected using one of the following methods:

- Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 2 hours.

- Electrical circuit protective systems shall have a fire-resistance rating of not less than 2 hours. Electrical circuit protective systems shall be installed in accordance with their listing requirements.

- Construction having a fire-resistance rating of not less than 2 hours.

Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operations.

Assembly (1)

13-1.2: 2hr, Steel Studs

3007.9 Standpipe Hose Connection

A Class I standpipe hose connection in accordance with Section 905 shall be provided in the interior exit stairway and ramp having direct access from the enclosed fire service access elevator lobby.

3007.9.1 Access

The exit enclosure containing the standpipe shall have access to the floor without passing through the enclosed fire service access elevator lobby.

Section 3008 Occupant Evacuation Elevators

Diagram

UpCodes Diagram (1)

Occupant Evacuation Elevator Lobbies

3008.1 General

Where elevators are to be used for occupant self-evacuation during fires, all passenger elevators for general public use shall comply with Sections 3008.1 through 3008.10. Where other elevators are used for occupant self-evacuation, those elevators shall comply with these sections.

3008.1.1

Reserved.

3008.1.2 Additional Exit Stairway

Diagram

Where an additional means of egress is required in accordance with Section 403.5.2, an additional exit stairway shall not be required to be installed in buildings provided with occupant evacuation elevators complying with Section 3008.1.

UpCodes Diagram (1)

High Rise: Additional Stairway

3008.1.3 Fire Safety and Evacuation Plan

The building shall have an approved fire safety and evacuation plan in accordance with the applicable requirements of Section 404 of the California Fire Code. The fire safety and evacuation plan shall incorporate specific procedures for the occupants using evacuation elevators.

3008.1.4 Operation

The occupant evacuation elevators shall be used for occupant self-evacuation in accordance with the occupant evacuation operation requirements in California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders, and the building's fire safety and evacuation plan.

3008.2 Automatic Sprinkler System

The building shall be equipped throughout with an approved, electrically supervised automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3008.2.1.

3008.2.1 Prohibited Locations

Automatic sprinklers shall not be installed in elevator machine rooms, machinery spaces, control rooms, control spaces and elevator hoistways of occupant evacuation elevators in accordance with this section and Section 3005.4.1.

3008.2.2 Sprinkler System Monitoring

The automatic sprinkler system shall have a sprinkler control valve supervisory switch and water-flow-initiating device provided for each floor that is monitored by the building's fire alarm system.

3008.3 Water Protection

Water from the operation of an automatic sprinkler system outside the enclosed lobby shall be prevented from infiltrating into the hoistway enclosure in accordance with an approved method.

3008.4 Shunt Trip

Means for elevator shutdown in accordance with Section 3005.5 shall not be installed on elevator systems used for occupant evacuation elevators.

3008.5 Hoistway Enclosure Protection

Occupant evacuation elevator hoistways shall be located in shaft enclosures complying with Section 713.

3008.5.1 Structural Integrity of Hoistway Enclosures

Occupant evacuation elevator hoistway enclosures shall comply with Sections 403.2.2.1 through 403.2.2.4.

3008.6 Occupant Evacuation Elevator Lobby

Diagram

Occupant evacuation elevators shall open into an enclosed elevator lobby in accordance with Sections 3008.6.1 through 3008.6.6. Egress is permitted through the elevator lobby in accordance with Item 1 of Section 1016.2.

UpCodes Diagram (1)

Primary

Occupant Evacuation Elevator Lobbies

3008.6.1 Access to Interior Exit Stairway or Ramp

The occupant evacuation elevator lobby shall have direct access from the enclosed elevator lobby to an interior exit stairway or ramp.

Exceptions:

- Access to an interior exit stairway or ramp shall be permitted to be through a protected path of travel that has a level of fire protection not less than the elevator lobby enclosure. The protected path shall be separated from the enclosed elevator lobby through an opening protected by a smoke and draft control assembly in accordance Section 716.2.2.1.1.

- Elevators that only service an open parking garage and the elevator lobby of the building shall not be required to provide direct access.

3008.6.2 Elevator Lobby Separation

Assembly

The occupant evacuation elevator lobby shall be separated from each floor with a smoke barrier in accordance with Section 709, except that lobby doorways shall comply with Section 3008.6.3.

Exception: Occupant evacuation elevator lobbies are not required to be separated at the levels of exit discharge.

Assemblies (2)

14-1.1: 1hr, Wood Joist

13-1.1: 1hr Steel Studs

Building products (3)

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

3008.6.3 Elevator Lobby Doorways

Diagram

Other than the doors to elevator machine rooms, machinery spaces, control rooms and control spaces in the smoke barrier, each doorway to an occupant evacuation elevator lobby shall be provided with a 3/4-hour fire door assembly complying with Section 716. Such a fire door assembly shall comply with the smoke and draft control assembly requirements of Section 716.2.2.1.1 and be tested in accordance with UL 1784 without an artificial bottom seal.

UpCodes Diagram (1)

Door Fire Ratings in Protective Wall Assemblies

Building products (4)

GPX® Ballistic

SaftiFirst

SuperClear® 45-HS

SaftiFirst

SuperClear® 45-HS-LI

SaftiFirst

SuperLite® X-45/60/90

SaftiFirst

3008.6.3.1 Vision Panel

A vision panel shall be installed in each fire door assembly in the smoke barrier. The vision panel shall consist of fire-protection-rated glazing, shall comply with the requirements of Section 716 and shall be located to furnish clear vision of the occupant evacuation elevator lobby.

3008.6.3.2 Door Closing

Each fire door assembly in the smoke barrier shall be automatic-closing upon receipt of any fire alarm signal from the emergency voice/alarm communication system serving the building.

3008.6.4 Lobby Size

Each occupant evacuation elevator lobby shall have minimum floor area as follows:

- The occupant evacuation elevator lobby floor area shall accommodate, at 3 square feet (0.28 m2) per person, not less than 25 percent of the occupant load of the floor area served by the lobby.

- The occupant evacuation elevator lobby floor area shall accommodate one wheelchair space of 30 inches by 52 inches (760 mm by 1320 mm) for each 50 persons, or portion thereof, of the occupant load of the floor area served by the lobby.

Exception: The size of lobbies serving multiple banks of elevators shall have the minimum floor area approved on an individual basis and shall be consistent with the building's fire safety and evacuation plan.

3008.6.5 Signage

An approved sign indicating elevators are suitable for occupant self-evacuation shall be posted on all floors adjacent to each elevator call station serving occupant evacuation elevators.

3008.6.6 Two-Way Communication System

A two-way communication system shall be provided in each occupant evacuation elevator lobby for the purpose of initiating communication with the fire command center or an alternate location approved by the fire department. The two-way communication system shall be designed and installed in accordance with Sections 1009.8.1 and 1009.8.2.

3008.7 Elevator System Monitoring

The occupant evacuation elevators shall be continuously monitored at the fire command center or a central control point approved by the fire department and arranged to display all of the following information:

- Floor location of each elevator car.

- Direction of travel of each elevator car.

- Status of each elevator car with respect to whether it is occupied.

- Status of normal power to the elevator equipment, elevator machinery and electrical apparatus cooling equipment where provided, elevator machine room, control room and control space ventilation and cooling equipment.

- Status of standby or emergency power system that provides backup power to the elevator equipment, elevator machinery and electrical cooling equipment where provided, elevator machine room, control room and control space ventilation and cooling equipment.

- Activation of any fire alarm initiating device in any elevator lobby, elevator machine room, machine space containing a motor controller or electric driving machine, control space, control room or elevator hoistway.

3008.7.1 Elevator Recall

The fire command center or an alternate location approved by the fire department shall be provided with the means to manually initiate a Phase I Emergency Recall of the occupant evacuation elevators in accordance with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3008.8 Electrical Power

The following features serving each occupant evacuation elevator shall be supplied by both normal power and Type 60/Class 2/Level 1 standby power:

- Elevator equipment.

- Ventilation and cooling equipment for elevator machine rooms, control rooms, machinery spaces and control spaces.

- Elevator car lighting.

3008.8.1 Determination of Standby Power Load

Standby power loads shall be based on the determination of the number of occupant evacuation elevators in Section 3008.1.1.

3008.8.2 Protection of Wiring or Cables

Assembly

Wires or cables that are located outside of the elevator hoistway, machine room, control room and control space and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to occupant evacuation elevators shall be protected using one of the following methods:

- Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 2 hours.

- Electrical circuit protective systems shall have a fire-resistance rating of not less than 2 hours. Electrical circuit protective systems shall be installed in accordance with their listing requirements.

- Construction having a fire-resistance rating of not less than 2 hours.

Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operation.

Assembly (1)

13-1.2: 2hr, Steel Studs

3008.9 Emergency Voice/Alarm Communication System

The building shall be provided with an emergency voice/alarm communication system. The emergency voice/alarm communication system shall be accessible to the fire department. The system shall be provided in accordance with Section 907.5.2.2.

3008.9.1 Notification Appliances

Not fewer than one audible and one visible notification appliance shall be installed within each occupant evacuation elevator lobby.

3008.10 Hazardous Material Areas

Diagram

Building areas shall not contain hazardous materials exceeding the maximum allowable quantities per control area as addressed in Section 414.2.

UpCodes Diagram (1)

Hazmat Control Areas

Section 3009 Private Residence Elevators

3009.1 General

The design, construction and installation of elevators installed within a residential dwelling unit or installed to provide access to one individual residential dwelling unit shall conform to California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3009.2 Hoistway Enclosures

Hoistway enclosures shall comply with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

3009.3 Hoistway Opening Protection

Hoistway landing doors for private residence elevators shall comply with California Code of Regulations, Title 8, Division 1, Chapter 4, Subchapter 6, Elevator Safety Orders.

Section 3010 Special Requirements for Elevators in Hospitals

3010.1 General

[OSHPD 1] In hospital buildings, all elevators shall comply with the provisions of this section.

3010.1.1 Seismic Switch

The seismic switch, as required by ASME A17.1, shall be connected to the essential electrical system.

3010.1.2 Annunciator

Either a visible or an audible annunciator shall be connected to the essential electrical system and be located in the elevator machine room. The annunciator will indicate if the seismic switch is inoperative due to a loss of power. If a visual annunciator is used, it shall be clearly visible in the room.

3010.1.3 Travel Speed

After a seismic switch has been triggered, the elevator shall have the ability to operate at a "go slow" speed until the elevator can be inspected. "Go slow" speed is defined as a travel speed of not more than 150 feet per minute (45.72 meters per minute).

3010.1.4 Cable-Operated Elevators

For cable-operated elevators, an additional sensor switch shall be installed on the governor rope/sheave. The sensor shall prevent car movement when the governor tail sheave is dislodged from its normal position.