Chapter 4 Special Detailed Requirements Based on Occupancy and Use

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE
CHAPTER 4 — SPECIAL DETAILED REQUIREMENTS BASED ON OCCUPANCY AND USE

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC- CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter | X |  |  |  |  |  |  | X | X | X | X | X |  | X | X | X |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) |  |  | X | X | X |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.2.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.3.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.4.7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.4.7.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.4.8.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.5.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 403.7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 404.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 404.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 404.12 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.2.1 |  |  | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.2.2 |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.2.3 |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.2.7 |  |  |  | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.3.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.6.4.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.8.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.9.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.9.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 406.9.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.2.7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.3.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.3.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.3.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.3.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.3.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.3.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.4 Reserved |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.4.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.4.5 — 407.4.5.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.7 — 407.7.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.10 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.11 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.12 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 407.13 — 407.13.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.2.7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.1.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.2.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.6.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.6.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.6.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.8.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.10 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.11 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.3.12 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Table 408.3.13 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.4.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.5.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.8.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.9.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.12 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.13 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.14 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.3.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.3.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.15.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 408.16 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 410.2.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 411.1 — 411.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 411.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 412.2.6 |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 414.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Table 414.2.5(3) |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 414.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 414.5.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.12.1.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.13 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.13.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.13.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 415.13.3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.1 |  |  | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.5 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.6.1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.6.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.7 Reserved |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.8 Reserved |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.10 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.11.1 |  |  | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.12 |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.13 |  |  | X | X |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.14 |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 420.15 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 421.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 422.1 |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |
| 422.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 422.3.2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 422.3.4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 422.6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 422.7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 435 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 436 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 439 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 440 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 441 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 442 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 443 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 444 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 446 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 449 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 450 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 452 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 453 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 455 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 4 provides detailed criteria for special uses and occupancies. The unique characteristics of a live/work unit as opposed to a 30-story high-rise building call for specific standards for each. Twenty-seven sections address covered and open mall buildings, atriums, hospitals, stages, buildings where hazardous materials are used and stored, jails and prisons, ambulatory care facilities and storm shelters, among other special occupancy issues.

ICC code Development note: Code change proposals to sections preceded by the designation [F], [BF] or [BE] will be considered by a code development committee meting during the 2024 (Group A) Code Development Cycle. All other code change proposals will be considered by a code development committee meeting during the 2025 (Group B) Code Development Cycle.

Section 401 Scope

401.1 Detailed Occupancy and Use Requirements

In addition to the occupancy and construction requirements in this code, the provisions of this chapter apply to the occupancies and use described herein.

Section 402 Covered Mall and Open Mall Buildings

Diagram

UpCodes Diagrams (2)

Fire Partitions: Mall Tenant Fire Separation

Gross Leasable Area

Building products (7)

Integrated Plumbing System / Aerofoil - TSL.IPS.AERO

The Splash Lab

Lumashelf Integrated Sink - TSL.LUMA

The Splash Lab

Monolith A Series - TSL.MON.A

The Splash Lab

Monolith B Series - TSL.MON.B

The Splash Lab

Monolith C Series - TSL.MON.C

The Splash Lab

Monolith D Series - TSL.MON.D

The Splash Lab

The Aerofoil Basin - TSL.AERO

The Splash Lab

402.1 Applicability

The provisions of this section shall apply to buildings or structures defined herein as covered or open mall buildings not exceeding three floor levels at any point nor more than three stories above grade plane. Except as specifically required by this section, covered and open mall buildings shall meet applicable provisions of this code.

Exceptions:

- Foyers and lobbies of Group B, R-1 and R-2 occupancies are not required to comply with this section.

- Buildings need not comply with the provisions of this section where they totally comply with other applicable provisions of this code.

402.1.1 Open Mall Building Perimeter Line

For the purpose of this code, a perimeter line shall be established. The perimeter line shall encircle all buildings and structures that comprise the open mall building and shall encompass any open-air interior walkways, open-air courtyards or similar open-air spaces. The perimeter line shall define the extent of the open mall building. Anchor buildings and parking structures shall be outside of the perimeter line and are not considered as part of the open mall building.

402.2 Open Space

A covered mall building and attached anchor buildings and parking garages shall be surrounded on all sides by a permanent open space or not less than 60 feet (18 288 mm). An open mall building and anchor buildings and parking garages adjoining the perimeter line shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm).

Exception: The permanent open space of 60 feet (18 288 mm) shall be permitted to be reduced to not less than 40 feet (12 192 mm), provided that the following requirements are met:

- The reduced open space shall not be allowed for more than 75 percent of the perimeter of the covered or open mall building and anchor buildings.

- The exterior wall facing the reduced open space shall have a fire-resistance rating of not less than 3 hours.

- Openings in the exterior wall facing the reduced open space shall have opening protectives with a fire protection rating of not less than 3 hours.

- Group E, H, I or R occupancies are not located within the covered or open mall building or anchor buildings.

402.3 Lease Plan

Each owner of a covered mall building or of an open mall building shall provide both the building and fire departments with a lease plan showing the location of each occupancy and its exits after the certificate of occupancy has been issued. Modifications or changes in occupancy or use from that shown on the lease plan shall not be made without prior approval of the building official.

402.4 Construction

Diagram

The construction of covered and open mall buildings, anchor buildings and parking garages associated with a mall building shall comply with Sections 402.4.1 through 402.4.3.

UpCodes Diagram (1)

Anchor Buildings and Mall Fire Separation

402.4.1 Area and Types of Construction

The building area and type of construction of covered mall or open mall buildings, anchor buildings and parking garages shall comply with this section.

402.4.1.1 Covered and Open Mall Buildings

Diagram

The building area of any covered mall or open mall building shall not be limited provided that the covered mall or open mall building does not exceed three floor levels at any point nor three stories above grade plane, and is of Type I, II, III or IV construction.

UpCodes Diagram (1)

Anchor Buildings and Mall Fire Separation

402.4.1.2 Anchor Buildings

The building area and building height of any anchor building shall be based on the type of construction as required by Section 503 as modified by Sections 504 and 506.

Exception: The building area of any anchor building shall not be limited provided that the anchor building is not more than three stories above grade plane, and is of Type I, II, III or IV construction.

402.4.1.3 Parking Garage

The building area and building height of any parking garage shall be based on the type of construction as required by Sections 406.5 and 406.6, respectively.

402.4.2 Fire-Resistance-Rated Separation

Fire-resistance-rated separation is not required between tenant spaces and the mall. Fire-resistance-rated separation is not required between a food court and adjacent tenant spaces or the mall.

402.4.2.1 Tenant Separations

Diagram

Each tenant space shall be separated from other tenant spaces by a fire partition complying with Section 708. A tenant separation wall is not required between any tenant space and the mall.

UpCodes Diagram (1)

Primary

Fire Partitions: Mall Tenant Fire Separation

402.4.2.2 Anchor Building Separation

Assembly

Diagram

An anchor building shall be separated from the covered or open mall building by fire walls complying with Section 706.

Exceptions:

- Anchor buildings of not more than three stories above grade plane that have an occupancy classification the same as that permitted for tenants of the mall building shall be separated by 2-hour fire-resistance-rated fire barriers complying with Section 707.

- The exterior walls of anchor buildings separated from an open mall building by an open mall shall comply with Table 705.5.

UpCodes Diagrams (2)

Primary

Anchor Buildings and Mall Fire Separation

Fire & Smoke: Walls vs. Barriers vs. Partitions

Assemblies (7)

12-1.2: 2hr, Wood

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

4-1.1: Concrete Walls

3-1.1 thru 3-1.4: CMU walls

14-1.5: 2hr, Wood

13-1.2: 2hr, Steel Studs

402.4.2.2.1 Openings Between Anchor Building and Mall

Except for the separation between Group R-1 sleeping units and the mall, openings between anchor buildings of Type IA, IB, IIA or IIB construction and the mall need not be protected.

402.4.2.3 Parking Garages

An attached garage for the storage of passenger vehicles having a capacity of not more than nine persons and open parking garages shall be considered as a separate building where it is separated from the covered or open mall building or anchor building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

Parking garages, which are separated from covered mall buildings, open mall buildings or anchor buildings, shall comply with the provisions of Table 705.5.

Pedestrian walkways and tunnels that connect garages to mall buildings or anchor buildings shall be constructed in accordance with Section 3104.

402.4.3 Open Mall Construction

Floor assemblies in, and roof assemblies over, the open mall of an open mall building shall be open to the atmosphere for not less than 20 feet (6096 mm), measured perpendicular from the face of the tenant spaces on the lowest level, from edge of balcony to edge of balcony on upper floors and from edge of roof line to edge of roof line. The openings within, or the unroofed area of, an open mall shall extend from the lowest/grade level of the open mall through the entire roof assembly. Balconies on upper levels of the mall shall not project into the required width of the opening.

402.4.3.1 Pedestrian Walkways

Pedestrian walkways connecting balconies in an open mall shall be located not less than 20 feet (6096 mm) from any other pedestrian walkway.

[F] 402.5 Automatic Sprinkler System

Covered and open mall buildings and buildings connected shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, which shall comply with all of the following:

- The automatic sprinkler system shall be complete and operative throughout occupied space in the mall building prior to occupancy of any of the tenant spaces. Unoccupied tenant spaces shall be similarly protected unless provided with approved alternative protection.

- Sprinkler protection for the mall of a covered mall building shall be independent from that provided for tenant spaces or anchor buildings.

- Sprinkler protection for the tenant spaces of an open mall building shall be independent from that provided for anchor buildings.

- Sprinkler protection shall be provided beneath exterior circulation balconies located adjacent to an open mall.

- Where tenant spaces are supplied by the same system, they shall be independently controlled.

Exception: An automatic sprinkler system shall not be required in spaces or areas of open parking garages separated from the covered or open mall building in accordance with Section 402.4.2.3 and constructed in accordance with Section 406.5.

402.6 Interior Finishes and Features

Interior finishes within the mall and installations within the mall shall comply with Sections 402.6.1 through 402.6.4.

402.6.1 Interior Finish

Interior wall and ceiling finishes within the mall of a covered mall building and within the exits of covered or open mall buildings shall have a minimum flame spread index and smoke-developed index of Class B in accordance with Chapter 8. Interior floor finishes shall meet the requirements of Section 804.

402.6.2 Kiosks

Kiosks and similar structures (temporary or permanent) located within the mall of a covered mall building or within the perimeter line of an open mall building shall meet the following requirements:

- Combustible kiosks or other structures shall not be located within a covered or open mall unless constructed of any of the following materials:

  - Fire-retardant-treated wood complying with Section 2303.2.

  - Foam plastics having a maximum heat release rate not greater than 100 kW (105 Btu/h) when tested in accordance with the exhibit booth protocol in UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source.

  - Aluminum composite material (ACM) meeting the requirements of Class A interior finish in accordance with Chapter 8 when tested as an assembly in the maximum thickness intended.

- Kiosks or similar structures located within the mall shall be provided with approved automatic sprinkler system and detection devices.

- The horizontal separation between kiosks or groupings thereof and other structures within the mall shall be not less than 20 feet (6096 mm).

- Each kiosk or similar structure or groupings thereof shall have an area not greater than 300 square feet (28 m2).

402.6.3 Play Structures

Play structures located within a mall building or within the perimeter line of an open mall building shall comply with Section 424. The horizontal separation between play structures, kiosks and similar structures within the mall shall be not less than 20 feet (6096 mm).

402.6.4 Plastic Signs

Plastic signs affixed to the storefront of any tenant space facing a mall or open mall shall be limited as specified in Sections 402.6.4.1 through 402.6.4.5.

402.6.4.1 Area

Plastic signs shall be not more than 20 percent of the wall area facing the mall.

402.6.4.2 Height and Width

Plastic signs shall be not greater than 36 inches (914 mm) in height, except that where the sign is vertical, the height shall be not greater than 96 inches (2438 mm) and the width shall be not greater than 36 inches (914 mm).

402.6.4.3 Location

Plastic signs shall be located not less than 18 inches (457 mm) from adjacent tenants.

402.6.4.4 Plastics Other Than Foam Plastics

Plastics other than foam plastics used in signs shall be light-transmitting plastics complying with Section 2606.4 or shall have a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D1929, and a flame spread index not greater than 75 and smoke-developed index not greater than 450 when tested in the manner intended for use in accordance with ASTM E84 or UL 723 or meet the acceptance criteria of Section 803.1.1.1 when tested in accordance with NFPA 286.

402.6.4.4.1 Encasement

Edges and backs of plastic signs in the mall shall be fully encased in metal.

402.6.4.5 Foam Plastics

Foam plastics used in signs shall have flame-retardant characteristics such that the sign has a maximum heat-release rate of 150 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source, and the foam plastics shall have the physical characteristics specified in this section. Foam plastics used in signs installed in accordance with Section 402.6.4 shall not be required to comply with the flame spread and smoke-developed indices specified in Section 2603.3.

402.6.4.5.1 Density

The density of foam plastics used in signs shall be not less than 20 pounds per cubic foot (pcf) (320 kg/ m3).

402.6.4.5.2 Thickness

The thickness of foam plastic signs shall not be greater than 1/2 inch (12.7 mm).

[F] 402.7 Emergency Systems

Covered and open mall buildings, anchor buildings and associated parking garages shall be provided with emergency systems complying with Sections 402.7.1 through 402.7.5.

[F] 402.7.1 Standpipe System

Diagram

Covered and open mall buildings shall be equipped throughout with a standpipe system as required by Section 905.3.3.

UpCodes Diagrams (2)

Standpipe Types

Standpipe System Classes

[F] 402.7.2 Smoke Control

Atriums connecting three or more stories in a covered mall building shall be provided with a smoke control system in accordance with Section 909.

[F] 402.7.3 Emergency Power

Covered mall buildings greater than 50,000 square feet (4645 m2) in area and open mall buildings greater than 50,000 square feet (4645 m2) within the established perimeter line shall be provided with emergency power that is capable of operating the emergency voice/alarm communication system in accordance with Section 2702.

[F] 402.7.4 Emergency Voice/Alarm Communication System

Where the total floor area is greater than 50,000 square feet (4645 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided.

The fire department shall have access to any emergency voice/alarm communication systems serving a mall, required or otherwise. The systems shall be provided in accordance with Section 907.5.2.2.

[F] 402.7.5 Fire Department Access to Equipment

Rooms or areas containing controls for air-conditioning systems or fire protection systems shall be identified for use by the fire department.

[BE] 402.8 Means of Egress

Covered mall buildings, open mall buildings and each tenant space within a mall building shall be provided with means of egress as required by this section and this code. Where there is a conflict between the requirements of this code and the requirements of Sections 402.8.1 through 402.8.8, the requirements of Sections 402.8.1 through 402.8.8 shall apply.

[BE] 402.8.1 Mall Width

For the purpose of providing required egress, malls are permitted to be considered as corridors but need not comply with the requirements of Section 1005.1 of this code where the width of the mall is as specified in this section.

[BE] 402.8.1.1 Minimum Width

The aggregate clear egress width of the mall in either a covered or open mall building shall be not less than 20 feet (6096 mm). The mall width shall be sufficient to accommodate the occupant load served. Any portion of the minimum required aggregate egress width shall be not less than 10 feet (3048 mm) measured to a height of 8 feet (2438 mm) between any projection of a tenant space bordering the mall and the nearest kiosk, vending machine, bench, display opening, food court or other obstruction to means of egress travel.

[BE] 402.8.2 Determination of Occupant Load

The occupant load permitted in any individual tenant space in a covered or open mall building shall be determined as required by this code. Means of egress requirements for individual tenant spaces shall be based on the occupant load thus determined.

[BE] 402.8.2.1 Occupant Formula

Diagram

In determining required means of egress of the mall, the number of occupants for whom means of egress are to be provided shall be based on gross leasable area of the covered or open mall building (excluding anchor buildings) and the occupant load factor as determined by Equation 4-1.

Equation 4-1

where:

OLF = The occupant load factor (square feet per person).

GLA = The gross leasable area (square feet).

Exception: Tenant spaces attached to a covered or open mall building but with a means of egress system that is totally independent of the open mall of an open mall building or of a covered mall building shall not be considered as gross leasable area for determining the required means of egress for the mall building.

UpCodes Diagrams (2)

Primary

Gross Leasable Area

Gross vs. Net Area

[BE] 402.8.2.2 OLF Range

The occupant load factor (OLF) is not required to be less than 30 and shall not exceed 50.

[BE] 402.8.2.3 Anchor Buildings

The occupant load of anchor buildings opening into the mall shall not be included in computing the total number of occupants for the mall.

[BE] 402.8.2.4 Food Courts

The occupant load of a food court shall be determined in accordance with Section 1004. For the purposes of determining the means of egress requirements for the mall, the food court occupant load shall be added to the occupant load of the covered or open mall building as calculated in Section 402.8.2.1.

[BE] 402.8.3 Number of Means of Egress

Wherever the distance of travel to the mall from any location within a tenant space used by persons other than employees is greater than 75 feet (22 860 mm) or the tenant space has an occupant load of 50 or more, not fewer than two means of egress shall be provided.

[BE] 402.8.4 Arrangements of Means of Egress

Assembly occupancies with an occupant load of 500 or more located within a covered mall building shall be so located such that their entrance will be immediately adjacent to a principal entrance to the mall and shall have not less than one-half of their required means of egress opening directly to the exterior of the covered mall building. Assembly occupancies located within the perimeter line of an open mall building shall be permitted to have their main exit open to the open mall.

[BE] 402.8.4.1 Anchor Building Means of Egress

Required means of egress for anchor buildings shall be provided independently from the mall means of egress system. The occupant load of anchor buildings opening into the mall shall not be included in determining means of egress requirements for the mall. The path of egress travel of malls shall not exit through anchor buildings. Malls terminating at an anchor building where other means of egress has not been provided shall be considered as a dead-end mall.

[BE] 402.8.5 Distance to Exits

Within each individual tenant space in a covered or open mall building, the distance of travel from any point to an exit or entrance to the mall shall be not greater than 200 feet (60 960 mm).

The distance of travel from any point within a mall of a covered mall building to an exit shall be not greater than 200 feet (60 960 mm). The maximum distance of travel from any point within an open mall to an exit or to the perimeter line of the open mall building shall be not greater than 200 feet (60 960 mm).

[BE] 402.8.6 Access to Exits

Where more than one exit is required, they shall be so arranged that it is possible to travel in either direction from any point in a mall of a covered mall building to separate exits or from any point in an open mall of an open mall building to two separate locations on the perimeter line, provided that neither location is an exterior wall of an anchor building or parking garage. The width of an exit passageway or corridor from a mall shall be not less than 66 inches (1676 mm).

Exception: Access to exits is permitted by way of a dead-end mall that does not exceed a length equal to twice the width of the mall measured at the narrowest location within the dead-end portion of the mall.

[BE] 402.8.6.1 Exit Passageways

Diagram

Where exit passageways provide a secondary means of egress from a tenant space, the exit passageways shall be constructed in accordance with Section 1024.

UpCodes Diagrams (2)

Exit Passageways: Construction (IBC)

Exit Passageway Usage

[BE] 402.8.7 Service Areas Fronting on Exit Passageways

Assembly

Mechanical rooms, electrical rooms, building service areas and service elevators are permitted to open directly into exit passageways, provided that the exit passageway is separated from such rooms with not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire protection rating of openings in the fire barriers shall be not less than 1 hour.

Assemblies (3)

WP 1292: 1hr, 40-44 STC, Steel Stud & Insulation

13-1.1: 1hr Steel Studs

FC 1105: 1hr, 50-54 STC, Conc & Steel Joist

[BE] 402.8.8 Security Grilles and Doors

Diagram

Horizontal sliding or vertical security grilles or doors that are a part of a required means of egress shall conform to the following:

- Doors and grilles shall remain in the full open position during the period of occupancy by the general public.

- Doors or grilles shall not be brought to the closed position when there are 10 or more persons occupying spaces served by a single exit or 50 or more persons occupying spaces served by more than one exit.

- The doors or grilles shall be openable from within without the use of any special knowledge or effort where the space is occupied.

- Where two or more exits are required, not more than one-half of the exits shall be permitted to include either a horizontal sliding or vertical rolling grille or door.

UpCodes Diagram (1)

Security Grilles

Section 403 High-Rise Buildings and Group I-2 Occupancies Having Occupied Floors Located More Than 75 Feet Above the Lowest Level of Fire Department Vehicle Access

403.1 Applicability

New high-rise buildings (see Section 202 for definition of a high-rise) and new Group I-2 occupancies having occupied floors located more than 75 feet above the lowest level of fire department vehicle access shall comply with Sections 403.2 through 403.7.

Exceptions: The provisions of Sections 403.2 through 403.7 shall not apply to the following buildings and structures:

- Airport traffic control towers in accordance with Section 412.2.

- Open parking garages in accordance with Section 406.5.

- The portion of a building containing a Group A-5 occupancy in accordance with Section 303.6.

- Special industrial occupancies in accordance with Section 503.1.1.

- Buildings such as power plants, lookout towers, steeples, grain houses and similar structures with noncontinuous human occupancy, when so determined by the enforcing agency.

For existing high-rise buildings and for existing Group R occupancies, see California Fire Code Chapter 11 and California Existing Building Code.

For the purpose of this section, in determining the level from which the highest occupied floor is to be measured, the enforcing agency should exercise reasonable judgment, including consideration of overall accessibility to the building by fire department personnel and vehicular equipment. When a building is located on sloping terrain and there is building access on more than one level, the enforcing agency may select the level that provides the most logical and adequate fire department access.

403.2 Construction

The construction of high-rise buildings shall comply with the provisions of Sections 403.2.1 through 403.2.3.

403.2.1 Reduction in Fire-Resistance Rating

The fire-resistance rating reductions specified in Sections 403.2.1.1 and 403.2.1.2 shall be allowed in buildings that have sprinkler control valves equipped with supervisory initiating devices and water-flow initiating devices for each floor.

Exception: Buildings, or portions of buildings, classified as a Group H-1, H-2 or H-3 occupancy.

403.2.1.1 Type of Construction

The following reductions in the minimum fire-resistance rating of the building elements in Table 601 shall be permitted as follows:

- For buildings not greater than 420 feet (128 m) in building height, the fire-resistance rating of the building elements in Type IA construction shall be permitted to be reduced to the minimum fire-resistance ratings for the building elements in Type IB.

Exception: The required fire-resistance rating of the primary structural frame shall not be reduced.

- In other than Group F-1, H-2, H-3, H-5, M and S-1 occupancies, the fire-resistance rating of the building elements in Type IB construction shall be permitted to be reduced to the fire-resistance ratings in Type IIA.

Exception: The required fire-resistance rating of the primary structural frame shall not be permitted to be reduced.

- The building height and building area limitations of a building containing building elements with reduced fire-resistance ratings shall be permitted to be the same as the building without such reductions.

403.2.1.2 Shaft Enclosures

For buildings not greater than 420 feet (128 m) in building height, the required fire-resistance rating of the fire barriers enclosing vertical shafts, other than interior exit stairway and elevator hoistway enclosures, is permitted to be reduced to 1 hour where automatic sprinklers are installed within the shafts at the top and at alternate floor levels.

[BS] 403.2.2 Structural Integrity of Interior Exit Stairways and Elevator Hoistway Enclosures

For high-rise buildings of Risk Category III or IV in accordance with Section 1604.5, and for all buildings that are more than 420 feet (128 m) in building height, enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Sections 403.2.2.1 through 403.2.2.4.

[BS] 403.2.2.1 Wall Assembly Materials

Where an interior exit stairway enclosure or an elevator hoistway enclosure is constructed as an interior wall of the building, the panels applied to the exterior of the enclosure shall be in accordance with one of the following:

- The wall assembly shall incorporate not fewer than two layers of impact-resistant panels, each of which meets or exceeds Soft Body Impact Classification Level 2 and Hard Body Impact Classification Level 2 as measured by the test method described in ASTM C1629/C1629M.

- The wall assembly shall incorporate not fewer than one layer of impact-resistant panels that meet or exceed Soft Body Impact Classification Level 2 and Hard Body Impact Classification Level 3 as measured by the test method described in ASTM C1629/C1629M.

- The wall assembly incorporates multiple layers of any material, tested in tandem, that meets or exceeds Soft Body Impact Classification Level 2 and Hard Body Impact Classification Level 3 as measured by the test method described in ASTM C1629/C1629M.

[BS] 403.2.2.2 Concrete and Masonry Walls

Concrete or masonry walls shall be deemed to satisfy the requirements of Section 403.2.2.1.

[BS] 403.2.2.3 Other Wall Assemblies

Any other wall assembly that provides impact resistance equivalent to that required by Section 403.2.2.1 for Soft Body Impact Classification Level 2 and for Hard Body Impact Classification Level 3, as measured by the test method described in ASTM C1629/C1629M, shall be permitted.

[BS] 403.2.2.4 Glass Walls

Glass walls complying with the safety glazing impact requirements of CPSC 16 CFR 1201, Cat. II or ANSI Z97.1, Class A shall be deemed to satisfy the requirements of Section 403.2.2.1.

[BF] 403.2.3 Sprayed Fire-Resistive Materials (SFRM)

The bond strength of the sprayed fire-resistive materials (SFRM) installed throughout the building shall be in accordance with Table 403.2.3.

TABLE 403.2.3—MINIMUM BOND STRENGTH

| HEIGHT OF BUILDINGa | SFRM MINIMUM BOND STRENGTH |
| --- | --- |
| Up to 420 feet | 430 psf |
| Greater than 420 feet | 1,000 psf |

For SI: 1 foot = 304.8 mm, 1 pound per square foot (psf) = 0.0479 kW/m2.

- Above the lowest level of fire department vehicle access.

[F] 403.3 Automatic Sprinkler System

Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a secondary water supply where required by Section 403.3.3. A sprinkler water-flow alarm-initiating device and a control valve with a supervisory signal-initiating device shall be provided at the lateral connection to the riser for each floor.

Exception: An automatic sprinkler system shall not be required in spaces or areas of telecommunications equipment buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided that those spaces or areas are equipped throughout with an automatic fire detection system in accordance with Section 907.2 and are separated from the remainder of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or not less than 2-hour horizontal assemblies constructed in accordance with Section 711, or both.

[F] 403.3.1 Number of Sprinkler System Risers and System Design

The number of sprinkler risers and system design shall comply with Section 403.3.1.1 or 403.3.1.2, based on building height.

[F] 403.3.1.1 Buildings 420 Feet or Less in Height

In buildings 420 feet (128 m) or less in height, sprinkler systems shall be supplied by a single standpipe or sprinkler express riser within each vertical water supply zone.

[F] 403.3.1.2 Buildings More Than 420 Feet in Height

In buildings more than 420 feet (128 m) in height, not fewer than two standpipes or sprinkler express risers or combination standpipe system risers shall supply automatic sprinkler systems within each vertical water supply zone and located in separate shafts. Each standpipe or sprinkler express riser or combination standpipe system riser shall supply automatic sprinkler systems on alternating floors within the vertical water supply zone such that two adjacent floors are not supplied from the same riser. Each sprinkler system shall be hydraulically designed so that when one connection is shut down, the other connection shall be capable of supplying the sprinkler system design demand.

[F] 403.3.1.3 Riser Location

Standpipes or sprinkler express risers shall be placed in interior exit stairways and ramps that are remotely located in accordance with Section 1007.1.

[F] 403.3.2 Water Supply to Required Fire Pumps

In all buildings having an occupied floor that is more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, in building height and buildings of Type IV-A and IV-B construction that are more than 120 feet (36 576 mm) in building height, required fire pumps shall be supplied by connections to not fewer than two water mains located in different streets. Separate supply piping shall be provided between each connection to the water main and the pumps. Each connection and the supply piping between the connection and the pumps shall be sized to supply the flow and pressure required for the pumps to operate.

Exception: Two connections to the same main shall be permitted provided that the main is valved such that an interruption can be isolated so that the water supply will continue without interruption through not fewer than one of the connections.

403.3.2.1 Fire Pumps

Redundant fire pump systems shall be required for high-rise buildings having an occupied floor more than 200 feet above the lowest level of fire department vehicle access. Each fire pump system shall be capable of automatically supplying the required demand for the automatic sprinkler and standpipe systems.

[F] 403.3.3 Secondary Water Supply

An automatic secondary on-site water supply having a usable capacity of not less than the hydraulically calculated sprinkler demand, including the hose stream requirement in accordance with Section 903.3.1.1, shall be provided for high-rise buildings and Group I-2 occupancies having occupied floors located more than 75 ft above the lowest level of fire department vehicle access assigned to Seismic Design Category C, D, E or F as determined by Section 1613. An additional fire pump shall not be required for the secondary water supply unless needed to provide the minimum design intake pressure at the suction side of the fire pump supplying the automatic sprinkler system. The secondary water supply shall have a duration of not less than 30 minutes as determined by the occupancy hazard classification in accordance with Section 903.3.1.1. The Class I standpipe system demand shall not be required to be included in the secondary on-site water supply calculations. In no case shall the secondary on-site water supply be less than 15,000 gallons.

[F] 403.3.4 Fire Pump Room

Fire pumps shall be located in rooms protected in accordance with Section 913.2.1.

403.3.5 Fire Pumps

See Section 913.6.

[F] 403.4 Emergency Systems

The detection, alarm and emergency systems of high-rise buildings shall comply with Sections 403.4.1 through 403.4.8.

[F] 403.4.1 Smoke Detection

Smoke detection shall be provided in accordance with Section 907.2.13.1.

[F] 403.4.2 Fire Alarm System

A fire alarm system shall be provided in accordance with Section 907.2.13.

[F] 403.4.3 Standpipe System

A high-rise building shall be equipped with a standpipe system as required by Section 905.3.

[F] 403.4.4 Emergency Voice/Alarm Communication System

An emergency voice/alarm communication system shall be provided in accordance with Section 907.5.2.2.

[F] 403.4.5 Emergency Communication Coverage

In-building, two-way emergency responder communication coverage shall be provided in accordance with Section 510 of the California Fire Code.

[F] 403.4.6 Fire Command

A fire command center complying with Section 911 shall be provided in a location approved by the fire code official.

403.4.7 Smoke Control System

All portions of high-rise buildings shall be provided with a smoke control system in accordance with Section 909.

[F] 403.4.8 Standby and Emergency Power

A standby power system complying with Section 2702 and Section 3003 shall be provided for the standby power loads specified in Section 403.4.8.3. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 403.4.8.4.

[F] 403.4.8.1 Equipment Room

If the standby or emergency power system includes a generator set inside a building, the system shall be located in a separate room enclosed with 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. System supervision with manual start and transfer features shall be provided at the fire command center.

Exception: In Group I-2, Condition 2, manual start and transfer features for the critical branch of the emergency power are not required to be provided at the fire command center.

[F] 403.4.8.2 Fuel Line Piping Protection

Fuel lines supplying a generator set inside a building shall be separated from areas of the building other than the room the generator is located in by one of the following methods:

- A fire-resistant pipe-protection system that has been tested in accordance with UL 1489. The system shall be installed as tested and in accordance with the manufacturer's installation instructions, and shall have a rating of not less than 2 hours. Where the building is protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1, the required rating shall be reduced to 1 hour.

- An assembly that has a fire-resistance rating of not less than 2 hours. Where the building is protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the required fire-resistance rating shall be reduced to 1 hour.

- Other approved methods.

[F] 403.4.8.3 Standby Power Loads

The following are classified as standby power loads:

- Ventilation and automatic fire detection equipment for smokeproof enclosures.

- Elevators.

- Where elevators are provided in a high-rise building for accessible means of egress, fire service access or occupant self-evacuation, the standby power system shall also comply with Sections 1009.4, 3007 or 3008, as applicable.

[F] 403.4.8.4 Emergency Power Loads

The following are classified as emergency power loads:

- Exit signs and means of egress illumination required by Chapter 10.

- Elevator car lighting.

- Emergency voice/alarm communications systems.

- Automatic fire detection systems.

- Fire alarm systems.

- Electrically powered fire pumps.

- Power and lighting for the fire command center required by Section 403.4.6.

[BE] 403.5 Means of Egress and Evacuation

The means of egress in high-rise buildings shall comply with Sections 403.5.1 through 403.5.5.

[BE] 403.5.1 Remoteness of Interior Exit Stairways

Required interior exit stairways shall be separated by a distance not less than 30 feet (9144 mm) or not less than one-fourth of the length of the maximum overall diagonal dimension of the building or area to be served, whichever is less. The distance shall be measured in a straight line between the nearest points of the enclosure surrounding the interior exit stairways. In buildings with three or more interior exit stairways, not fewer than two of the interior exit stairways shall comply with this section. Interlocking or scissor stairways shall be counted as one interior exit stairway.

[BE] 403.5.2 Additional Interior Exit Stairway

For buildings other than Group R-2 and their ancillary spaces that are more than 420 feet (128 m) in building height, one additional interior exit stairway meeting the requirements of Sections 1011 and 1023 shall be provided in addition to the minimum number of exits required by Section 1006.3. The total capacity of any combination of remaining interior exit stairways with one interior exit stairway removed shall be not less than the total capacity required by Section 1005.1. Scissor stairways shall not be considered the additional interior exit stairway required by this section.

Exceptions:

- An additional interior exit stairway shall not be required to be installed in buildings having elevators used for occupant self-evacuation in accordance with Section 3008.

- An additional interior exit stairway shall not be required for other portions of the building where the highest occupiable floor level in those areas is less than 420 feet (128 m) in building height.

[BE] 403.5.3 Stairway Door Operation

Stairway doors other than the exit discharge doors shall be permitted to be locked from the stairway side. Stairway doors that are locked from the stairway side shall be capable of being unlocked without unlatching where any of the following conditions occur:

- Individually or simultaneously upon a signal from the fire command center.

- Simultaneously upon activation of a fire alarm signal in an area served by the stairway.

- Upon failure of the power supply to the lock or the locking system.

[BE] 403.5.3.1 Stairway Communication System

A telephone or other two-way communications system connected to an approved constantly attended station shall be provided at not less than every fifth floor in each stairway where the doors to the stairway are locked. Systems shall be listed in accordance with UL 2525 and installed in accordance with NFPA 72.

[BE] 403.5.4 Smokeproof Enclosures

Every exit enclosure in high-rise buildings shall comply with Sections 909.20 and 1023.12. Every required interior exit stairway in Group I-2 occupancies serving floors more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access shall be a smokeproof enclosure in accordance with Sections 909.20 and 1023.12.

Exception: In high-rise buildings, exit enclosures serving three or less adjacent floors where one of the adjacent floors is the level of exit discharge.

[BE] 403.5.5 Luminous Egress Path Markings

Luminous egress path markings shall be provided in accordance with Section 1025.

403.6 Elevators

Elevator installation and operation in high-rise buildings shall comply with Chapter 30 and Sections 403.6.1 and 403.6.2.

Enclosed elevator lobbies shall be provided in accordance with Section 3006. Exceptions 2. 3, 4 and 5 of 3006.3 shall only be permitted where approved by the Fire Chief in accordance with Section 1.11.2.1.1 or in accordance with Section 1.11.2.1.2 for all state-owned buildings, state-occupied buildings and state institutions throughout the state.

403.6.1 Fire Service Access Elevator

In buildings with an occupied floor more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, not fewer than two fire service access elevators, or all elevators, whichever is less, shall be provided in accordance with Section 3007. Each fire service access elevator shall have a capacity of not less than 3,500 pounds (1588 kg) and shall comply with Section 3002.4.

403.6.2 Occupant Evacuation Elevators

Where installed in accordance with Section 3008, passenger elevators for general public use shall be permitted to be used for occupant self-evacuation.

403.7 Existing High-Rise Buildings

For existing high-rise buildings, see California Fire Code Chapter 11 and California Existing Building Code.

Section 404 Atriums

404.1 General

Diagram

The provisions of Sections 404.1 through 404.12 shall apply to buildings containing atriums. Atriums are not permitted in buildings or structures classified as Group H.

Exception: Vertical openings that comply with Sections 712.1.1 through 712.1.3, and Sections 712.1.9 through 712.1.14.

UpCodes Diagrams (2)

Primary

Atrium

Exit Access Stair: Enclosure (Ex. 5)

404.2 Use

The floor of the atrium shall not be used for other than low fire hazard uses and only approved materials and decorations in accordance with the California Fire Code shall be used in the atrium space.

Exception: The atrium floor area is permitted to be used for any approved use where the individual space is provided with an automatic sprinkler system in accordance with Section 903.3.1.1.

[F] 404.3 Automatic Sprinkler Protection

Assembly

An approved automatic sprinkler system shall be installed throughout the entire building.

Exceptions:

- That area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

- Where the ceiling of the atrium is more than 55 feet (16 764 mm) above the floor, sprinkler protection at the ceiling of the atrium is not required.

Assembly (1)

13-1.2: 2hr, Steel Studs

[F] 404.4 Fire Alarm System

A fire alarm system shall be provided in accordance with Section 907.2.14.

404.5 Smoke Control

A smoke control system shall be installed in accordance with Section 909.

Exceptions:

- In other than Group I-2 and R-2.1, Condition 2, smoke control is not required for atriums that connect only two stories.

- A smoke control system is not required for atriums connecting more than two stories when all of the following are met:

  - Only the two lowest stories shall be permitted to be open to the atrium.

  - All stories above the lowest two stories shall be separated from the atrium in accordance with the provisions for a shaft in Section 713.4.

404.6 Enclosure of Atriums

Assembly

Diagram

Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section 711, or both.

Exceptions:

- A fire barrier is not required where a glass wall forming a smoke partition is provided. The glass wall shall comply with all of the following:

  - Automatic sprinklers are provided along both sides of the separation wall and doors, or on the room side only if there is not a walkway on the atrium side. The sprinklers shall be located between 4 inches and 12 inches (102 mm and 305 mm) away from the glass and at intervals along the glass not greater than 6 feet (1829 mm). The sprinkler system shall be designed so that the entire surface of the glass is wet upon activation of the sprinkler system without obstruction.

  - The glass wall shall be installed in a gasketed frame in a manner that the framing system deflects without breaking (loading) the glass before the sprinkler system operates.

  - Where glass doors are provided in the glass wall, they shall be either self-closing or automatic-closing.

- A fire barrier is not required where a glass-block wall assembly complying with Section 2110 and having a 3/4-hour fire protection rating is provided.

- In other than Group I and R-2.1 occupancies, a fire barrier is not required between the atrium and the adjoining spaces of up to three floors of the atrium provided that such spaces are accounted for in the design of the smoke control system.

- In other than Group I and R-2.1 occupancies, a fire barrier is not required between the atrium and the adjoining spaces where the atrium is not required to be provided with a smoke control system.

- In Group I-2 and R-2.1 occupancies, a fire barrier is not required between the atrium and the adjoining spaces, other than care recipient sleeping or treatment rooms, for up to three stories of the atrium provided that such spaces are accounted for in the design of the smoke control system and do not provide access to care recipient sleeping or treatment rooms.

- A horizontal assembly is not required between the atrium and openings for escalators complying with Section 712.1.3.

- A horizontal assembly is not required between the atrium and openings for exit access stairways and ramps complying with Item 4 of Section 1019.3.

UpCodes Diagrams (2)

Door Fire Ratings in Protective Wall Assemblies

Exit Stairways in Atriums

Assemblies (3)

WP 1292: 1hr, 40-44 STC, Steel Stud & Insulation

14-1.1: 1hr, Wood Joist

13-1.1: 1hr Steel Studs

Building products (3)

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

[F] 404.7 Standby Power

Diagram

Equipment required to provide smoke control shall be provided with standby power in accordance with Section 909.11.

UpCodes Diagram (1)

Standby Power Systems

404.8 Interior Finish

The interior finish of walls and ceilings of the atrium shall be not less than Class B. Sprinkler protection shall not result in a reduction in class.

[BE] 404.9 Exit Access Travel Distance

Diagram

Exit access travel distance for areas open to an atrium shall comply with the requirements of Section 1017.

UpCodes Diagrams (5)

Primary

Atriums: Exiting, Pt. 1

Primary

Exit Stairways in Atriums

Travel Distance Measurement

Example: Exit Access Travel Distance

Travel Distance to Area of Refuge

[BE] 404.10 Exit Stairways in an Atrium

Diagram

Where an atrium contains an interior exit stairway all the following shall be met:

- The entry to the exit stairway is the edge of the closest riser of the exit stairway.

- The entry of the exit stairway shall have access from a minimum of two directions.

- The distance between the entry to an exit stairway in an atrium and the entrance to a minimum of one exit stairway enclosed in accordance with Section 1023.2 shall comply with the separation required by Section 1007.1.1.

- Exit access travel distance shall be measured to the closest riser of the exit stairway.

- Not more than 50 percent of the exit stairways shall be located in the same atrium.

- The discharge from the exit stairway at the level of exit discharge shall comply with Section 1028.1.

UpCodes Diagrams (2)

Primary

Exit Stairways in Atriums

Exit Separation Measurement Points

[BE] 404.11 Interior Exit Stairway Discharge

Diagram

Discharge of interior exit stairways through an atrium shall be in accordance with Section 1028.

UpCodes Diagram (1)

Primary

Exit Stairways in Atriums

404.12 Group I and R-2.1 Occupancy Means of Egress

Required means of egress from sleeping and treatment rooms in Group I and R-2.1 occupancies shall not pass through the atrium.

Section 405 Underground Buildings

405.1 General

Diagram

The provisions of Sections 405.2 through 405.9 apply to building spaces having a floor level used for human occupancy more than 30 feet (9144 mm) below the finished floor of the lowest level of exit discharge.

Exceptions: The provisions of Section 405 are not applicable to the following buildings or portions of buildings:

- One- and two-family dwellings, sprinklered in accordance with Section 903.3.1.3.

- Parking garages provided with automatic sprinkler systems in compliance with Section 405.3.

- Fixed guideway transit systems.

- Grandstands, bleachers, stadiums, arenas and similar facilities.

- Where the lowest story is the only story that would qualify the building as an underground building and has an area not greater than 1,500 square feet (139 m2) and has an occupant load less than 10.

- Pumping stations and other similar mechanical spaces intended only for limited periodic use by service or maintenance personnel.

UpCodes Diagram (1)

Level of Exit Discharge

405.2 Construction Requirements

The underground portion of the building shall be of Type I construction.

[F] 405.3 Automatic Sprinkler System

The highest level of exit discharge serving the underground portions of the building and all levels below shall be equipped with an automatic sprinkler system installed in accordance with Section 903.3.1.1. Water-flow switches and control valves shall be supervised in accordance with Section 903.4.

405.4 Compartmentation

Compartmentation shall be in accordance with Sections 405.4.1 through 405.4.3.

405.4.1 Number of Compartments

A building having a floor level more than 60 feet (18 288 mm) below the finished floor of the lowest level of exit discharge shall be divided into not fewer than two compartments of approximately equal size. Such compartmentation shall extend through the highest level of exit discharge serving the underground portions of the building and all levels below.

Exception: The lowest story need not be compartmented where the area is not greater than 1,500 square feet (139 m2) and has an occupant load of less than 10.

405.4.2 Smoke Barrier Penetration

Diagram

The compartments shall be separated from each other by a smoke barrier in accordance with Section 709. Penetrations between the two compartments shall be limited to plumbing and electrical piping and conduit that are firestopped in accordance with Section 714. Doorways shall be protected by fire door assemblies that comply with Section 716, automatic-closing by smoke detection in accordance with Section 716.2.6.6 and installed in accordance with NFPA 105 and Section 716.2.2.1. Where provided, each compartment shall have an air supply and an exhaust system independent of the other compartments.

UpCodes Diagram (1)

Smoke Partitions vs. Smoke Barriers

Building products (6)

SuperLite® I

SaftiFirst

SuperLite® I-XL

SaftiFirst

SuperLite® I-XL IGU

SaftiFirst

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

405.4.3 Elevators

Where elevators are provided, each compartment shall have direct access to an elevator. Where an elevator serves more than one compartment, an enclosed elevator lobby shall be provided and shall be separated from each compartment by a smoke barrier in accordance with Section 709. Doorways in the smoke barrier shall be protected by fire door assemblies that comply with Section 716, shall comply with the smoke and draft control assembly requirements of Section 716.2.2.1 with the UL 1784 test conducted without an artificial bottom seal, and shall be automatic-closing by smoke detection in accordance with Section 716.2.6.6.

405.5 Smoke Control System

A smoke control system shall be provided in accordance with Sections 405.5.1 and 405.5.2.

405.5.1 Control System

A smoke control system is required to control the migration of products of combustion in accordance with Section 909 and the provisions of this section. Smoke control shall restrict movement of smoke to the general area of fire origin and maintain means of egress in a usable condition.

405.5.2 Compartment Smoke Control System

Where compartmentation is required, each compartment shall have an independent smoke control system. The system shall be automatically activated and capable of manual operation in accordance with Sections 907.2.18 and 907.2.19.

[F] 405.6 Fire Alarm Systems

A fire alarm system shall be provided where required by Sections 907.2.18 and 907.2.19.

[BE] 405.7 Means of Egress

Means of egress shall be in accordance with Sections 405.7.1 and 405.7.2.

[BE] 405.7.1 Number of Exits

Each floor level shall be provided with not fewer than two exits. Where compartmentation is required by Section 405.4, each compartment shall have not fewer than one exit and not fewer than one exit access doorway into the adjoining compartment.

[BE] 405.7.2 Smokeproof Enclosure

Every required stairway serving floor levels more than 30 feet (9144 mm) below the finished floor of its level of exit discharge shall comply with the requirements for a smokeproof enclosure as provided in Section 1023.12.

[F] 405.8 Standby and Emergency Power

A standby power system complying with Section 2702 shall be provided for the standby power loads specified in Section 405.8.1. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 405.8.2.

[F] 405.8.1 Standby Power Loads

Diagram

The following are classified as standby power loads:

- Smoke control system.

- Ventilation and automatic fire detection equipment for smokeproof enclosures.

- Elevators, as required in Section 3003.

UpCodes Diagram (1)

Standby Power Systems

[F] 405.8.2 Emergency Power Loads

The following are classified as emergency power loads:

- Emergency voice/alarm communications systems.

- Fire alarm systems.

- Automatic fire detection systems.

- Elevator car lighting.

- Means of egress and exit sign illumination as required by Chapter 10.

- Fire pumps.

[F] 405.9 Standpipe System

Diagram

The underground building shall be equipped throughout with a standpipe system in accordance with Section 905.

UpCodes Diagrams (2)

Standpipe Types

Standpipe System Classes

Section 406 Motor-Vehicle-Related Occupancies

Diagram

UpCodes Diagrams (3)

Open Parking Garage vs. Open Parking Structure requirements

Enclosed Parking Garage Ventilation - Ducted System

Enclosed Parking Garage Ventilation - Ductless Jet-Induction System

406.1 General

All motor-vehicle-related occupancies shall comply with Section 406.2. Private garages and carports shall also comply with Section 406.3. Open public parking garages shall also comply with Sections 406.4 and 406.5. Enclosed public parking garages shall also comply with Sections 406.4 and 406.6. Motor fuel-dispensing facilities shall also comply with Section 406.7. Repair garages shall also comply with Section 406.8.

406.2 Design

Diagram

Private garages and carports, open and enclosed public parking garages, motor fuel-dispensing facilities and repair garages shall comply with Sections 406.2.1 through 406.2.9.

UpCodes Diagrams (2)

Primary

Open Parking Garage vs. Open Parking Structure requirements

Private Garage Separation from Dwelling Units (BC)

Building product (1)

FOAMULAR® NGX® 400/600/1000

Owens Corning

406.2.1 Automatic Garage Door Operators and Vehicular Gates

Where provided, automatic garage door operators shall be listed and labeled in accordance with UL 325. Where provided, automatic vehicular gates shall comply with Section 3110. See Health and Safety Code Sections 19890, 19891 and 19892 for additional provisions for residential garage door openers.

406.2.2 Clear Height

The clear height of each floor level in vehicle and pedestrian traffic areas shall be not less than 7 feet (2134 mm). Canopies under which fuels are dispensed shall have a clear height in accordance with Section 406.7.2. [DSA-AC, HCD 1-AC] The clear height of vehicle and pedestrian areas required to be accessible shall comply with Chapter 11A or 11B, as applicable.

Exception: A lower clear height is permitted for a parking tier in mechanical-access open parking garages where approved by the building official.

[BE] 406.2.3 Accessible Parking Spaces

Diagram

Where parking is provided, accessible parking spaces, access aisles and vehicular routes serving accessible parking shall be provided in accordance with Chapter 11A or Chapter 11B, as applicable.

UpCodes Diagram (1)

Multiple Parking Lots on a Site

406.2.4 Floor Surfaces

Floor surfaces shall be of concrete or similar approved noncombustible and nonabsorbent materials. The area of floor used for the parking of automobiles or other vehicles shall be sloped to facilitate the movement of liquids to a drain or toward the main vehicle entry doorway. The surface of vehicle fueling pads in motor fuel-dispensing facilities shall be in accordance with Section 406.7.1.

Exceptions:

- Asphalt parking surfaces shall be permitted at ground level for public parking garages and private carports.

- Slip-resistant, nonabsorbent, interior floor finishes having a critical radiant flux not more than 0.45 W/cm2, as determined by ASTM E648 or NFPA 253, shall be permitted in repair garages.

406.2.5 Sleeping Rooms

Openings between a motor vehicle-related occupancy and a room used for sleeping purposes shall not be permitted.

406.2.6 Fuel Dispensing

The dispensing of fuel shall only be permitted in motor fuel-dispensing facilities in accordance with Section 406.7.

406.2.7 Electric Vehicle Charging Stations and Systems

Diagram

Where provided, electric vehicle charging systems shall be installed in accordance with the California Electrical Code and the California Green Building Standards Code. Electric vehicle charging system equipment shall be listed and labeled in accordance with UL 2202. Electric vehicle supply equipment shall be listed and labeled in accordance with UL 2594. Accessibility to electric vehicle charging stations shall be provided in accordance with Chapters 11A and/or 11B.

UpCodes Diagrams (3)

EV Charging Station Location within a Site

EV Charging Station Clearances

EV Accessible Charging Stations

406.2.8 Mixed Occupancies and Uses

Diagram

Mixed uses shall be allowed in the same building as public parking garages and repair garages in accordance with Section 508.1. Mixed uses in the same building as an open parking garage are subject to Sections 402.4.2.3, 406.5.11, 508.1, 510.3, 510.4 and 510.7.

UpCodes Diagram (1)

Open Parking Garage Beneath Groups A, I, B, M and R

406.2.9 Equipment and Appliances

Equipment and appliances shall be installed in accordance with Sections 406.2.9.1 through 406.2.9.3 and the California Mechanical Code, California Plumbing Code and California Electrical Code.

406.2.9.1 Elevation of Ignition Sources

Diagram

Equipment and appliances having an ignition source and located in hazardous locations and public garages, private garages, repair garages, automotive motor fuel-dispensing facilities and parking garages shall be elevated such that the source of ignition is not less than 18 inches (457 mm) above the floor surface on which the equipment or appliance rests. For the purpose of this section, rooms or spaces that are not part of the living space of a dwelling unit and that communicate directly with a private garage through openings shall be considered to be part of the private garage.

Exception: Elevation of the ignition source is not required for appliances that are listed as flammable vapor ignition resistant.

UpCodes Diagrams (2)

Vehicular Barriers for Equipment: Examples

Water Heater: Garages

406.2.9.1.1 Parking Garages

Connection of a parking garage with any room in which there is a fuel-fired appliance shall be by means of a vestibule providing a two-doorway separation, except that a single door is permitted where the sources of ignition in the appliance are elevated in accordance with Section 406.2.9.

Exception: This section shall not apply to appliance installations complying with Section 406.2.9.2 or 406.2.9.3.

406.2.9.2 Public Garages

Diagram

Appliances located in public garages, motor fuel-dispensing facilities, repair garages or other areas frequented by motor vehicles shall be installed not less than 8 feet (2438 mm) above the floor. Where motor vehicles are capable of passing under an appliance, the appliance shall be installed at the clearances required by the appliance manufacturer and not less than 1 foot (305 mm) higher than the tallest vehicle garage door opening.

Exception: The requirements of this section shall not apply where the appliances are protected from motor vehicle impact and installed in accordance with Section 406.2.9.1 and NFPA 30A.

UpCodes Diagram (1)

Primary

Appliance Locations: Public and Private Garages

406.2.9.3 Private Garages

Diagram

Appliances located in private garages and carports shall be installed with a minimum clearance of 6 feet (1829 mm) above the floor.

Exception: The requirements of this section shall not apply where the appliances are protected from motor vehicle impact and are installed in accordance with Section 406.2.9.1.

UpCodes Diagrams (2)

Primary

Appliance Locations: Public and Private Garages

Vehicular Barriers for Equipment: Examples

406.3 Private Garages and Carports

Diagram

Private garages and carports shall comply with Sections 406.2 and 406.3, or they shall comply with Sections 406.2 and 406.4.

UpCodes Diagram (1)

Private Garage Separation from Dwelling Units (BC)

Building product (1)

Garage Door Fiberglass Insulation Kit

Owens Corning

406.3.1 Classification

Assembly

Private garages and carports shall be classified as Group U occupancies. Each private garage shall be not greater than 1,000 square feet (93 m2) in area. Multiple private garages are permitted in a building where each private garage is separated from the other private garages by 1-hour fire barriers in accordance with Section 707, or 1-hour horizontal assemblies in accordance with Section 711, or both.

Exception: The area of a private garage accessory to Group R-3 one- or two-family dwellings shall not be greater than 3,000 square feet in area.

Assemblies (5)

WP 3510: 1hr, Wood Studs

21-1.1: 1hr, Wood Joist

14-1.3: 1hr, Wood

26-1.1: 1hr, I-joist

25-1.1: 1hr, I-joist

Building products (7)

FF109-200 1 Hour Fire Rated LED Downlight Cover

Tenmat

FF109-250 1 Hour Fire Rated LED Downlight Cover

Tenmat

FF109-300 UL Fire Rated Recessed Light Cover

Tenmat

FF109-350 Fire Rated Light Cover

Tenmat

FF109-FRSC 1 Hour Fire Rated Speaker Cover

Tenmat

FF130 - 2x2 Fire Rated Troffer Cover

Tenmat

FF130 - 2x4 Fire Rated Troffer Cover

Tenmat

406.3.2 Separation

Diagram

For other than private garages adjacent to dwelling units, the separation of private garages from other occupancies shall comply with Section 508. Separation of private garages from dwelling units shall comply with Sections 406.3.2.1 and 406.3.2.2.

UpCodes Diagram (1)

Primary

Private Garage Separation from Dwelling Units (BC)

406.3.2.1 Dwelling Unit Separation

The private garage shall be separated from the dwelling unit and its attic area by means of gypsum board, not less than 1/2 inch (12.7 mm) in thickness, applied to the garage side. Garages beneath habitable rooms shall be separated from all habitable rooms above by not less than a 5/8-inch (15.9 mm) Type X gypsum board or equivalent and 1/2-inch (12.7 mm) gypsum board applied to structures supporting the separation from habitable rooms above the garage. Door openings between a private garage and the dwelling unit shall be equipped with either solid wood doors or solid or honeycomb core steel doors not less than 13/8 inches (34.9 mm) in thickness, or doors in compliance with Section 716.2.2.1 with a fire protection rating of not less than 20 minutes. Doors shall be self-closing and self-latching.

406.3.2.2 Ducts

Ducts in a private garage and ducts penetrating the walls or ceilings separating the dwelling unit from the garage, including its attic area, shall be constructed of sheet steel of not less than 0.019 inch (0.48 mm) in thickness and shall not have openings into the garage.

406.3.3 Carports

Diagram

Carports shall be open on not fewer than two sides. Carports open on fewer than two sides shall be considered to be a garage and shall comply with the requirements for private garages.

UpCodes Diagram (1)

Primary

Carport Requirements

406.3.3.1 Carport Separation

A separation is not required between a Group R-3 and U carport, provided that the carport is entirely open on two or more sides and there are not enclosed areas above.

406.4 Public Parking Garages

Diagram

Parking garages, other than private garages, shall be classified as public parking garages and shall comply with the provisions of Sections 406.2 and 406.4 and shall be classified as either an open parking garage or an enclosed parking garage. Open parking garages shall also comply with Section 406.5. Enclosed parking garages shall also comply with Section 406.6. See Section 510 for special provisions for parking garages.

UpCodes Diagram (1)

Primary

Open Parking Garage vs. Open Parking Structure requirements

406.4.1 Guards

Guards shall be provided in accordance with Section 1015. Guards serving as vehicle barriers shall comply with Sections 406.4.2 and 1015.

406.4.2 Vehicle Barriers

Vehicle barriers not less than 2 feet 9 inches (835 mm) in height shall be placed where the vertical distance from the floor of a drive lane or parking space to the ground or surface directly below is greater than 1 foot (305 mm). Vehicle barriers shall comply with the loading requirements of Section 1607.11.

Exception: Vehicle barriers are not required in vehicle storage compartments in a mechanical access parking garage.

406.4.3 Ramps

Diagram

Vehicle ramps shall not be considered as required exits unless pedestrian facilities are provided. Vehicle ramps that are utilized for vertical circulation as well as for parking shall not exceed a slope of 1 unit vertical in 15 units horizontal (6.67 percent slope).

UpCodes Diagram (1)

Parking Garage Exiting: Vehicular Ramps

406.5 Open Parking Garages

Diagram

Open parking garages shall comply with Sections 406.2, 406.4 and 406.5.

UpCodes Diagrams (5)

Primary

Open Parking Garage vs. Open Parking Structure requirements

Primary

Open Parking Garage

Sprinklers: Bldgs > 55 ft. (Ex. 1)

Open Parking Garage Beneath Groups A, I, B, M and R

Group B or M Buildings With Group S-2 Open Parking Garage Above

406.5.1 Construction

Open parking garages shall be of Type I, II or IV construction. Open parking garages shall meet the design requirements of Chapter 16. For vehicle barriers, see Section 406.4.2.

406.5.2 Openings

Diagram

For natural ventilation purposes, the exterior side of the structure shall have uniformly distributed openings on two or more sides. The area of such openings in exterior walls on a tier shall be not less than 20 percent of the total perimeter wall area of each tier. The aggregate length of the openings considered to be providing natural ventilation shall be not less than 40 percent of the perimeter of the tier. Interior walls shall be not less than 20 percent open with uniformly distributed openings.

Exception: Openings are not required to be distributed over 40 percent of the building perimeter where the required openings are uniformly distributed over two opposing sides of the building.

UpCodes Diagram (1)

Open Parking Garage

406.5.2.1 Openings Below Grade

Where openings below grade provide required natural ventilation, the outside horizontal clear space shall be one and one-half times the depth of the opening. The width of the horizontal clear space shall be maintained from grade down to the bottom of the lowest required opening.

406.5.3 Mixed Occupancies and Uses

Diagram

Mixed uses shall be allowed in the same building as an open parking garage subject to the provisions of Sections 402.4.2.3, 406.5.11, 508.1, 510.3, 510.4 and 510.7.

UpCodes Diagrams (3)

Podiums: Parking Beneath Group R

Open Parking Garage Beneath Groups A, I, B, M and R

Group S-2 Enclosed Parking Garage With Group S-2 Open Parking Garage Above

406.5.4 Area and Height

Area and height of open parking garages shall be limited as set forth in Chapter 5 for Group S-2 occupancies and as further provided for in Section 508.1.

TABLE 406.5.4—OPEN PARKING GARAGES AREA AND HEIGHT

| TYPE OF CONSTRUCTION | AREA PER TIER (square feet) | HEIGHT (in tiers) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Ramp access | Mechanical access |  |
|  |  |  | Automatic sprinkler system |  |
|  |  |  | No | Yes |
| IA | Unlimited | Unlimited | Unlimited | Unlimited |
| IB | Unlimited | 12 tiers | 12 tiers | 18 tiers |
| IIA | 50,000 | 10 tiers | 10 tiers | 15 tiers |
| IIB | 50,000 | 8 tiers | 8 tiers | 12 tiers |
| IV | 50,000 | 4 tiers | 4 tiers | 4 tiers |

For SI: 1 square foot = 0.0929 m2.

406.5.4.1 Single Use

Where the open parking garage is used exclusively for the parking or storage of private motor vehicles, and the building is without other uses, the area and height shall be permitted to comply with Table 406.5.4, along with increases allowed by Section 406.5.5.

Exception: The grade-level tier is permitted to contain an office, waiting and toilet rooms having a total combined area of not more than 1,000 square feet (93 m2). Such area need not be separated from the open parking garage.

In open parking garages having a spiral or sloping floor, the horizontal projection of the structure at any cross section shall not exceed the allowable area per parking tier. In the case of an open parking garage having a continuous spiral floor, each 9 feet 6 inches (2896 mm) of height, or portion thereof, shall be considered under these provisions to be a tier.

406.5.5 Area and Height Increases

The allowable area and height of open parking garages shall be increased in accordance with the provisions of this section. Garages with sides open on three-fourths of the building's perimeter are permitted to be increased by 25 percent in area and one tier in height. Garages with sides open around the entire building's perimeter are permitted to be increased by 50 percent in area and one tier in height. For a side to be considered open under these provisions, the total area of openings along the side shall be not less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm).

Allowable tier areas in Table 406.5.4 shall be increased for open parking garages constructed to heights less than the table maximum. The gross tier area of the garage shall not exceed that permitted for the higher structure. Not fewer than three sides of each such larger tier shall have continuous horizontal openings not less than 30 inches (762 mm) in clear height extending for not less than 80 percent of the length of the sides. All parts of such larger tier shall be not more than 200 feet (60 960 mm) horizontally from such an opening. In addition, each such opening shall face a street or yard with access to a street with a width of not less than 30 feet (9144 mm) for the full length of the opening, and standpipes shall be provided in each such tier.

Open parking garages of Type II construction, with all sides open, shall be unlimited in allowable area where the building height does not exceed 75 feet (22 860 mm). For a side to be considered open, the total area of openings along the side shall be not less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm). All portions of tiers shall be within 200 feet (60 960 mm) horizontally from such openings or other natural ventilation openings as defined in Section 406.5.2. These openings shall be permitted to be provided in courts with a minimum dimension of 20 feet (6096 mm) for the full width of the openings.

406.5.6 Fire Separation Distance

Exterior walls and openings in exterior walls shall comply with Table 601 and Table 705.5. The distance to an adjacent lot line shall be determined in accordance with Section 705 and Table 705.5.

[BE] 406.5.7 Means of Egress

Where persons other than parking attendants are permitted, open parking garages shall meet the means of egress requirements of Chapter 10. Where persons other than parking attendants are not permitted, there shall be not fewer than two exit stairways. Each exit stairway shall be not less than 36 inches (914 mm) in width. Lifts shall be permitted to be installed for use of employees only, provided that they are completely enclosed by noncombustible materials.

[F] 406.5.8 Standpipe System

Diagram

An open parking garage shall be equipped with a standpipe system as required by Section 905.3.

UpCodes Diagrams (2)

Standpipe Types

Standpipe System Classes

406.5.9 Enclosure of Vertical Openings

Enclosure shall not be required for vertical openings except as specified in Section 406.5.7.

406.5.10 Ventilation

Ventilation, other than the percentage of openings specified in Section 406.5.2, shall not be required.

406.5.11 Prohibitions

The following uses and alterations are not permitted:

- Vehicle repair work.

- Parking of buses, trucks and similar vehicles.

- Partial or complete closing of required openings in exterior walls by tarpaulins or any other means.

- Dispensing of fuel.

406.6 Enclosed Parking Garages

Diagram

Enclosed parking garages shall comply with Sections 406.2, 406.4 and 406.6.

UpCodes Diagrams (2)

Enclosed Parking Garage Ventilation - Ducted System

Enclosed Parking Garage Ventilation - Ductless Jet-Induction System

406.6.1 Heights and Areas

Diagram

Enclosed vehicle parking garages and portions thereof that do not meet the definition of open parking garages shall be limited to the allowable heights and areas specified in Sections 504 and 506 as modified by Section 507. Roof parking is permitted.

UpCodes Diagram (1)

Open Spaces for Unlimited Area Bldgs.

406.6.2 Ventilation

A mechanical ventilation system and exhaust system shall be provided in accordance with Chapters 4 and 5 of the California Mechanical Code.

Exception: Mechanical ventilation shall not be required for enclosed parking garages that are accessory to one- and two-family dwellings.

[F] 406.6.3 Automatic Sprinkler System

An enclosed parking garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.10.

406.6.4 Mechanical-Access Enclosed Parking Garages

Diagram

Mechanical-access enclosed parking garages shall be in accordance with Sections 406.6.4.1 through 406.6.4.4.

UpCodes Diagram (1)

Stories with Single Exits - Condition 3

406.6.4.1 Separation

Assembly

Mechanical-access enclosed parking garages shall be separated from other occupancies and accessory uses by not less than 2-hour fire barriers constructed in accordance with Section 707 or by not less than 2-hour horizontal assemblies constructed in accordance with Section 711, or both. Refer to Table 508.4 for additional requirements.

Assembly (1)

13-1.2: 2hr, Steel Studs

406.6.4.2 Smoke Removal

A mechanical smoke removal system, installed in accordance with Section 910.4, shall be provided for all areas containing a mechanical-access enclosed parking garage.

406.6.4.3 Fire Control Equipment Room

Fire control equipment, consisting of the fire alarm control unit, mechanical ventilation controls and an emergency shutdown switch, shall be provided in a room located where the equipment is able to be accessed by the fire service from a secured exterior door of the building. The room shall be not less than 50 square feet (4.65 m2) in area and shall be in a location that is approved by the fire code official.

Exception: A fire control room shall not be required where there is a fire command center provided in compliance with Section 911 of this code.

406.6.4.3.1 Emergency Shutdown Switch

The mechanical parking system shall be provided with a manually activated emergency shutdown switch for use by emergency personnel. The switch shall be clearly identified and shall be in a location approved by the fire code official.

406.6.4.4 Fire Department Access Doors

Access doors shall be provided in accordance with Section 3206.7 of the California Fire Code.

406.7 Motor Fuel-Dispensing Facilities

Motor fuel-dispensing facilities shall comply with the California Fire Code and Sections 406.2 and 406.7.

406.7.1 Vehicle Fueling Pad

The vehicle shall be fueled on noncoated concrete or other approved paving material having a resistance not exceeding 1 megohm as determined by the methodology in CEN EN 1081.

406.7.2 Canopies

Canopies under which fuels are dispensed shall have a clear, unobstructed height of not less than 13 feet 6 inches (4115 mm) to the lowest projecting element in the vehicle drive-through area. Canopies and their supports over pumps shall be of noncombustible materials, fire-retardant-treated wood complying with Chapter 23, heavy timber complying with Section 2304.11 or construction providing 1-hour fire resistance. Combustible materials used in or on a canopy shall comply with one of the following:

- Shielded from the pumps by a noncombustible element of the canopy, or heavy timber complying with Section 2304.11.

- Plastics covered by aluminum facing having a thickness of not less than 0.010 inch (0.30 mm) or corrosion-resistant steel having a base metal thickness of not less than 0.016 inch (0.41 mm). The plastic shall have a flame spread index of 25 or less and a smoke-developed index of 450 or less when tested in the form intended for use in accordance with ASTM E84 or UL 723 and a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D1929.

- Panels constructed of light-transmitting plastic materials shall be permitted to be installed in canopies erected over motor vehicle fuel-dispensing station fuel dispensers, provided that the panels are located not less than 10 feet (3048 mm) from any building on the same lot and face yards or streets not less than 40 feet (12 192 mm) in width on the other sides. The aggregate areas of plastics shall be not greater than 1,000 square feet (93 m2). The maximum area of any individual panel shall be not greater than 100 square feet (9.3 m2).

406.7.2.1 Canopies Used to Support Gaseous Hydrogen Systems

Canopies that are used to shelter dispensing operations where flammable compressed gases are located on the roof of the canopy shall be in accordance with the following:

- The canopy shall meet or exceed Type I construction requirements.

- Operations located under canopies shall be limited to refueling only.

- The canopy shall be constructed in a manner that prevents the accumulation of hydrogen gas.

[F] 406.8 Repair Garages

Repair garages shall be constructed in accordance with the California Fire Code and Sections 406.2 and 406.8. This occupancy shall not include motor fuel-dispensing facilities, as regulated in Section 406.7.

[F] 406.8.1 Ventilation

Repair garages shall be mechanically ventilated in accordance with the California Mechanical Code. The ventilation system shall be controlled at the entrance to the garage.

[F] 406.8.2 Gas Detection System

Repair garages used for repair of vehicles fueled by nonodorized gases including but not limited to hydrogen and nonodorized LNG, shall be provided with a gas detection system that complies with Section 916. The gas detection system shall be designed to detect leakage of nonodorized gaseous fuel. Where lubrication or chassis service pits are provided in garages used for repairing nonodorized LNG-fueled vehicles, gas sensors shall be provided in such pits.

[F] 406.8.2.1 System Activation

Activation of a gas detection alarm shall result in all of the following:

- Initiation of distinct audible and visual alarm signals in the repair garage, where the ventilation system is interlocked with gas detection.

- Deactivation of all heating systems located in the repair garage.

- Activation of the mechanical ventilation system, where the system is interlocked with gas detection.

[F] 406.8.2.2 Failure of the Gas Detection System

Failure of the gas detection system shall automatically deactivate the heating system, activate the mechanical ventilation system where the system is interlocked with the gas detection system, and cause a trouble signal to sound at an approved location.

[F] 406.8.3 Automatic Sprinkler System

A repair garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.9.1.

406.9 Electric Vehicle

[SFM]

406.9.1 Charging

In any building or interior area used for charging electric vehicles, electrical equipment shall be installed in accordance with the California Electrical Code.

406.9.2 Ventilation

Mechanical exhaust ventilation, when required by the California Electrical Code shall be provided at a rate as required by Article 625 or as required by Section 1202 of the California Building Code whichever is greater. The ventilation system shall include both the supply and exhaust equipment and shall be permanently installed and located to intake supply air from the outdoors and vent the exhaust directly to the outdoors without conducting the exhaust air through other spaces within the building.

Exception: Positive pressure ventilation systems shall only be allowed in buildings or areas that have been designed and approved for that application.

406.9.3 Electrical Interface

The electrical supply circuit to electrically powered mechanical ventilation equipment shall be interlocked with the recharging equipment used to supply the vehicle(s) being charged, and shall remain energized during the entire charging cycle. Electric vehicle recharging equipment shall be marked or labeled in accordance with the California Electrical Code.

Exceptions:

- Exhaust ventilation shall not be required in areas with an approved engineered ventilation system, which maintains a hydrogen gas concentration at less than 25 percent of the lower flammability limit.

- Mechanical exhaust ventilation for hydrogen shall not be required where the charging equipment utilized is installed and listed for indoor charging of electric vehicles without ventilation.

Section 407 Group I-2

Diagram

UpCodes Diagrams (6)

Waiting Areas in Medical Facilities (11B)

Corridor Widths in Hospitals

Group I-2: Direct Access to Corridor

Sprinkler Reqs. - Hospital Clothes Closets

Distance of Travel within Group I-2 Sleeping Room

Non-rated Doors in Group I-2 Corridors

Building products (2)

AquaSense® 5-3/8 in. Gooseneck Sensor Faucet With Gear-driven Ceramic Cartridge - ZG6920

Zurn

AquaSense® Wall Mount 5-3/8 in. Gooseneck Sensor Faucet With Gear-driven Ceramic Cartridge - ZG6922

Zurn

407.1 General

Occupancies in Group I-2 shall comply with the provisions of Sections 407.1 through 407.13 and other applicable provisions of this code.

407.1.1 Construction

Group I-2 occupancies wherein mental health patients are restrained shall be housed in buildings of Type IA or Type IB construction.

Exception: Occupancies in Group I-2 wherein mental health patients are restrained are permitted to be housed in one-story buildings of Type IIA, Type IIIA or Type VA construction provided the floor area does not exceed 5,200 square feet (483 m2) between fire walls of two-hour fire-resistive construction with openings protected by fire assemblies having a 11/2-hour fire protection rating.

407.2 Corridors Continuity and Separation

Diagram

Corridors in occupancies in Group I-2 shall be continuous to the exits and shall be separated from other areas in accordance with Section 407.3 except spaces conforming to Sections 407.2.1 through 407.2.6.

UpCodes Diagrams (2)

Nursing Home Areas Open to Corridors

Gift Shops in I-2 Corridors

407.2.1 Waiting and Similar Areas

Waiting areas and similar public-use areas or group meeting spaces constructed as required for corridors shall be permitted to be open to a corridor, only where all of the following criteria are met:

- The spaces are not occupied as care recipient's sleeping rooms, treatment rooms, incidental uses listed in Table 509, in accordance with Section 509, or hazardous uses.

- The open space is protected by an automatic fire detection system installed in accordance with Section 907.

- The corridors onto which the spaces open, in the same smoke compartment, are protected by an automatic smoke detection system installed in accordance with Section 907, and the smoke compartment in which the spaces are located is equipped throughout with quick-response sprinklers in accordance with Section 903.3.2.

- The space is arranged so as not to obstruct access to the required exits.

- Each space is located to permit direct visual supervision by the facility staff.

407.2.2 Nurse Stations

Spaces for care providers', supervisory staff, doctors' and nurses' charting, communications and related clerical areas shall be permitted to be open to, or located within the corridor, provided the required construction along the perimeter of the corridor is maintained. Construction of nurse stations or portions of nurse stations, within the envelope of the corridor is not required to be fire-resistive rated. Nurse stations in new and existing facilities see the California Code of Regulations, Title 19, Division 1, Chapter 1, Subchapter 1, Article 3, Section 3.11(d) for storage and equipment requirements.

In detention or secure mental health facilities, the provisions above applies to enclosed nurse stations within the corridor.

407.2.3 Psychiatric Treatment Areas

Areas wherein psychiatric care recipients who are incapable of self-preservation are housed, or group meeting or multipurpose therapeutic spaces other than incidental uses in accordance with Section 509, under continuous supervision by facility staff, shall be permitted to be open to the corridor, where the following criteria are met:

- Each area does not exceed 1,500 square feet (140 m2).

- The area is located to permit supervision by the facility staff.

- The area is arranged so as not to obstruct any access to the required exits.

- The area is equipped with an automatic fire detection system installed in accordance with Section 907.2.

- Not more than one such space is permitted in any one smoke compartment.

- The walls and ceilings of the space are constructed as required for corridors.

407.2.4 Gift Shops

Diagram

Gift shops and associated storage that are less than 500 square feet (455 m2) in area shall be permitted to be open to the corridor where such spaces are constructed as required for corridors.

UpCodes Diagram (1)

Primary

Gift Shops in I-2 Corridors

407.2.5 Nursing Home Housing Units

Diagram

In Group I-2, Condition 1 occupancies, in areas where nursing home residents are housed, shared living spaces, group meeting or multipurpose therapeutic spaces shall be permitted to be open to the corridor, where all of the following criteria are met:

- The walls and ceilings of the space are constructed as required for corridors.

- The spaces are not occupied as resident sleeping rooms, treatment rooms, incidental uses in accordance with Section 509, or hazardous uses.

- The open space is protected by an automatic smoke detection system installed in accordance with Section 907.

- The corridors onto which the spaces open, in the same smoke compartment, are protected by an automatic smoke detection system installed in accordance with Section 907, and the smoke compartment in which the spaces are located is equipped throughout with quick-response sprinklers in accordance with Section 903.3.2.

- The space is arranged so as not to obstruct access to the required exits.

- Each space is located to permit direct visual supervision by the facility staff.

UpCodes Diagram (1)

Group I-2 Nursing Homes

407.2.6 Nursing Home Cooking Facilities

In Group I-2, Condition 1 occupancies, rooms or spaces that contain a cooking facility with domestic cooking appliances shall be permitted in fully sprinklered buildings where all of the following criteria are met:

- The number of care recipients housed in the smoke compartment shall not be greater than 30.

- The number of care recipients served by the cooking facility shall not be greater than 30.

- Only one cooking facility area shall be permitted in a smoke compartment.

- The corridor shall be a clearly identified space delineated by construction or floor pattern, material or color.

- The space containing the domestic cooking facility shall be arranged so as not to obstruct access to the required exit.

- The cooking appliance shall comply with Section 407.2.7.

407.2.7 Domestic Cooking Appliances

In Group I-2 occupancies, installation of cooking appliances used in domestic cooking facilities shall comply with all of the following:

- The types of cooking appliances permitted shall be limited to ovens, cooktops, ranges, warmers and microwaves.

- Domestic cooking hoods installed and constructed in accordance with Section 505 of the California Mechanical Code shall be provided over cooktops and ranges.

- Cooktops and ranges shall be protected in accordance with Section 904.15.

- A shut-off for the fuel and electrical power supply to the cooking equipment shall be provided in a location to which only staff has access.

- A timer shall be provided that automatically deactivates the cooking appliances within a period of not more than 120 minutes.

- A portable fire extinguisher shall be provided. Installation shall be in accordance with Section 906, and the extinguisher shall be located a distance of travel of 30 feet (9144 mm) or less from each domestic cooking appliance.

Exceptions:

- Cooktops and ranges located within smoke compartments with no patient sleeping or patient care areas are not required to comply with Items 3, 4 and 5 of this section.

- Cooktops and ranges used for care recipient training or nutritional counseling are not required to comply with Item 3 of this section.

407.3 Corridor Wall Construction

Corridor walls shall be constructed as fire partitions in accordance with Section 708.

407.3.1 Corridor Doors

Diagram

In fully sprinklered buildings, corridor doors, other than those in a wall required to be rated by Section 509.4 or for the enclosure of a vertical opening or an exit, shall not have a required fire protection rating and shall not be required to be equipped with self-closing or automatic-closing devices, but shall provide an effective barrier to limit the transfer of smoke and shall be equipped with positive latching. In Group I-2 Occupancies, self-closing or automatic-closing devices are not required on corridor doors to patient sleeping rooms, treatment rooms and offices located in areas specified in Sections 1224 and 1225, excluding offices specified in Sections 1224.21 and 1225.8. Roller latches are not permitted. Other doors shall conform to Section 716.

UpCodes Diagram (1)

Door Fire Ratings in Protective Wall Assemblies

407.3.1.1 Door Construction

Corridor doors not required to have a fire protection rating shall comply with the following:

- Solid doors shall have close-fitting operational tolerances, head and jamb stops.

- Dutch-style doors shall have an astragal, rabbet or bevel at the meeting edges of the upper and lower door sections. Both the upper and lower door sections shall have latching hardware. Dutch-style doors shall have hardware that connects the upper and lower sections to function as a single leaf.

407.3.1.2 Swing of Corridor Doors

Corridor doors, other than those equipped with self-closing or automatic-closing devices shall not swing into the required width of corridors.

Exception: In detention and/or secure mental health facilities, doors may swing into required width of corridors as long as 44 inches clear is maintained with any one door open 90 degrees and clear corridor widths required in Chapter 12 can be maintained with doors open 180 degrees.

407.3.2 Glazing

In fully sprinklered buildings, fixed fully tempered or laminated glass in wood or metal frames may be used in corridor walls, provided the glazed area does not exceed 25 percent of the areas of the corridor wall of the room. The total area of glass in corridor walls is not limited when the glazing is fixed 1/3-hour fire-protection-rated glazing in approved frames and the size of individual glazed panel does not exceed 1,296 square inches (0.836 m2).

[BE] 407.4 Means of Egress

Group I-2 occupancies shall be provided with means of egress complying with Chapter 10 and Sections 407.4.1 through 407.4.4. The fire safety and evacuation plans provided in accordance with Section 1002.2 shall identify the building components necessary to support a defend-in-place emergency response in accordance with Sections 403 and 404 of the California Fire Code.

[BE] 407.4.1 Direct Access to a Corridor

Diagram

Habitable rooms in Group I-2 occupancies shall have an exit access door leading directly to a corridor.

Exceptions:

- Rooms with exit doors opening directly to the outside at ground level.

- Rooms arranged as care suites complying with Section 407.4.4.

UpCodes Diagram (1)

Primary

Group I-2: Direct Access to Corridor

[BE] 407.4.1.1 Locking Devices

Locking devices that restrict access to a care recipient's room from the corridor and that are operable only by staff from the corridor side shall not restrict the means of egress from the care recipient's room.

Exceptions:

- This section shall not apply to rooms in psychiatric treatment and similar care areas.

- Locking arrangements in accordance with Section 1010.2.13.

407.4.1.2 Basement Exits

All rooms below grade shall have not less than one exit access that leads directly to an exterior exit door opening directly to an exit discharge at grade plane or the public way.

[BE] 407.4.2 Distance of Travel

Diagram

The distance of travel between any point in a Group I-2 occupancy sleeping room, not located in a care suite, and an exit access door in that room shall be not greater than 50 feet (15 240 mm).

UpCodes Diagram (1)

Primary

Distance of Travel within Group I-2 Sleeping Room

407.4.2.1 Two Means of Egress

Any sleeping room of more than 1,000 square feet (93 m2) shall have no fewer than two exit access doors from the sleeping room located in accordance with Section 1007.1. Any room, other than sleeping rooms, with an area of more than 2,500 square feet (232 m2) shall have no fewer than two exit access doors from the room located in accordance with Section 1007.1.

[BE] 407.4.3

Reserved.

[BE] 407.4.4 Group I-2 Care Suites

Diagram

Care suites in Group I-2 shall comply with Sections 407.4.4.1 through 407.4.4.5 and either Section 407.4.4.6 or 407.4.4.7.

UpCodes Diagram (1)

Group I-2: Direct Access to Corridor

[BE] 407.4.4.1 Exit Access Through Care Suites

Exit access from all other portions of a building not classified as a care suite shall not pass through a care suite.

[BE] 407.4.4.2 Separation

Care suites shall be separated from other portions of the building, including other care suites, not less than a one-hour fire barrier complying with Section 707.

[BE] 407.4.4.3 Access to Corridor

Every care suite shall have a door leading directly to an exit access corridor or horizontal exit. Movement from habitable rooms within a care suite shall not require more than 100 feet (30 480 mm) of travel within the care suite to a door leading to the exit access corridor or horizontal exit. Where a care suite is required to have more than one exit access door by Section 407.4.4.6.2 or 407.4.4.7.2, the additional door shall lead directly to an exit access corridor, exit or an adjacent suite.

407.4.4.3.1 Sleeping Room

Sleeping rooms shall be limited to one intervening room.

407.4.4.3.2 Two Intervening Rooms

Movement from habitable rooms other than sleeping rooms located within a care suite, shall not require passage through more than two intervening rooms and 50 feet (15 240 mm) distance of exit access travel within the care suite.

Exception: The distance of travel shall be permitted to be increased to 100 feet (38 100 mm) where an automatic fire sprinkler system is provided throughout the Group I-2 fire area and an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72.

[BE] 407.4.4.4 Reserved

[BE] 407.4.4.5 Doors Within Care Suites

Doors in care suites serving habitable rooms shall be permitted to comply with one of the following:

- Manually operated horizontal sliding doors permitted in accordance with Exception 9 to Section 1010.1.2.

- Power-operated doors permitted in accordance with Section 1010.1.2, Exception 7.

- Means of egress doors complying with Section 1010.

[BE] 407.4.4.6 Care Suites Containing Sleeping Room Areas

Sleeping rooms shall be permitted to be grouped into care suites where one of the following criteria is met:

- The care suite is not used as an exit access for more than eight care recipient beds.

- The arrangement of the care suite allows for direct and constant visual supervision into the sleeping rooms by care providers.

- In fully sprinklered buildings, an automatic smoke detection system is provided in the sleeping rooms and installed in accordance with Section 907.2.6.2.2, Item 1 and NFPA 72.

[BE] 407.4.4.6.1 Area

Care suites containing sleeping rooms shall be not greater than 5,000 square feet (465 m2) in area.

Exceptions:

- Care suites containing sleeping rooms shall be permitted to be not greater than 7,500 square feet (696 m2) in area where an automatic fire sprinkler system is provided throughout the Group I-2 fire area.

- Care suites containing sleeping rooms shall be permitted to be not greater than 10,000 square feet (929 m2) in area where an automatic fire sprinkler system is provided throughout the Group I-2 fire area and where an automatic smoke detection system is provided throughout the care suite and installed in accordance with Section 907.

[BE] 407.4.4.6.2 Exit Access

Any sleeping room, or any care suite that contains sleeping rooms, of more than 1,000 square feet (93 m2) shall have not fewer than two exit access doors from the care suite located in accordance with Section 1007.

[BE] 407.4.4.7 Care Suites Not Containing Sleeping Rooms

Areas not containing sleeping rooms, but only treatment areas and the associated rooms, spaces or circulation space, shall be permitted to be grouped into care suites and shall conform to the limitations in Sections 407.4.4.7.1 and 407.4.4.7.2.

[BE] 407.4.4.7.1 Area

Care suites of rooms, other than sleeping rooms, shall have an area not greater than 10,000 square feet (929 m2).

[BE] 407.4.4.7.2 Exit Access

Any room or care suites, other than sleeping rooms, with an area of more than 2,500 square feet (232 m2) shall have not fewer than two exit access doors from the room or care suite located in accordance with Section 1007.

407.4.5 Group I-2 Nonpatient-Care Suites

The means of egress provisions for nonpatient-care suites shall be in accordance with the primary use and occupancy of the suite.

407.4.5.1 Separation

Nonpatient-care suites shall be separated from other portions of the building, including other suites, by not less than a 1-hour fire barrier complying with Section 707. Each suite of rooms shall be separated from the remainder of the building by not less than a 1-hour fire barrier.

407.4.5.2 Area

Nonpatient-care suites of rooms shall have an area not greater than 10,000 square feet (929 m2).

407.4.5.3 Automatic Sprinkler System Protection

Nonpatient-care suites shall be located in fully sprinklered buildings.

[BE] 407.5 Smoke Barriers

Smoke barriers shall be provided to subdivide every story used by persons receiving care, treatment or sleeping into not fewer than two smoke compartments. Smoke barriers shall be provided to subdivide other stories with an occupant load of 50 or more persons, regardless of occupancy or use, into not fewer than two smoke compartments. The smoke barrier shall be in accordance with Section 709.

Exceptions:

- This requirement shall not apply to the following:

  - Any story, not containing a Group I-2 occupancy, that is located above a story containing a Group I-2 occupancy.

  - Areas that do not contain a Group I-2 occupancy, where such areas are separated from the Group I-2 occupancy by a horizontal exit in accordance with Section 1026.2.

  - Any story, not containing a Group I-2 occupancy, that is located more than one story below a story containing a Group I-2 occupancy.

  - Any story housing only mechanical equipment where such story is located below a story containing a Group I-2 occupancy and is separated from the story above by a horizontal assembly having not less than a 2 hour fire resistance-rating.

Building products (3)

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

[BE] 407.5.1 Smoke Compartment Size

Stories shall be divided into smoke compartments with an area of not more than 22,500 square feet (2092 m2) in Group I-2 occupancies.

Exceptions:

- A smoke compartment in Group I-2, Condition 2 is permitted to have an area of not more than 40,000 square feet (3716 m2) provided that all patient sleeping rooms within that smoke compartment are configured for single patient occupancy and any suite within the smoke compartment complies with Section 407.4.4.

- A smoke compartment in Group I-2, Condition 2 without patient sleeping rooms is permitted to have an area of not more than 40,000 square feet (3716 m2).

[BE] 407.5.2 Exit Access Travel Distance

Diagram

The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm).

UpCodes Diagrams (2)

Example: Exit Access Travel Distance

Travel Distance to Area of Refuge

[BE] 407.5.3 Refuge Area

Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:

- Not less than 30 net square feet (2.8 m2) for each care recipient confined to bed or stretcher.

- Not less than 6 square feet (0.56 m2) for each ambulatory care recipient not confined to bed or stretcher and for other occupants.

Areas or spaces permitted to be included in the calculation of refuge area are corridors, sleeping areas, treatment rooms, lounge or dining areas and other low-hazard areas.

[BE] 407.5.4 Independent Egress

A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated. Smoke compartments that do not contain an exit shall be provided with direct access to not less than two adjacent smoke compartments.

[BE] 407.5.5 Horizontal Assemblies

Horizontal assemblies supporting smoke barriers required by this section shall be designed to resist the movement of smoke. Elevator lobbies shall be in accordance with Section 3006.2.

407.6 Automatic-Closing Doors

Automatic-closing doors with hold-open devices shall comply with Sections 709.5 and 716.2.

407.6.1 Activation of Automatic-Closing Doors

Automatic-closing doors on hold-open devices in accordance with Section 716.2.6.6 shall also close upon activation of a fire alarm system, an automatic sprinkler system, or both. The automatic release of the hold-open device on one door shall release all such doors within the same smoke compartment.

[F] 407.7 Automatic Sprinkler System

Every facility as specified herein wherein more than six clients or patients are housed or cared for on the premises on a 24-hour per-day-basis shall have installed and maintained in an operable condition in every building or portion thereof where clients or patients are housed, an automatic sprinkler system of a type approved by the state fire marshal. The provisions of this subsection shall apply to every person, firm or corporation establishing, maintaining or operating a hospital, children's home, children's nursery or institution, or a home or institution for the care of aged or persons with dementia or other cognitive impairments, or any institution for persons with mental illness or persons with developmental disabilities and any nursing or convalescent home, and to any state-owned or state-occupied building used for any of the types of facilities specified herein.

Exceptions:

- This section shall not apply to homes or institutions for the 24-hour-per-day care of ambulatory children if all of the following conditions are satisfied:

  - The buildings or portions thereof in which children are housed are not more than two stories in height and are constructed and maintained in accordance with regulations adopted by the state fire marshal.

  - The buildings or portions thereof housing more than six such children shall have installed and maintained in an operable condition therein, a fire alarm system of a type approved by the state fire marshal. Such system shall be activated by detectors responding to invisible particles of combustion other than heat, except that detectors used in closets, usable under-floor areas, storage rooms, bathrooms, attached garages, attics, plenums, laundry rooms and rooms of similar use, may be heat-responsive devices.

  - The building or portions thereof do not house persons with mental illness or children with developmental disabilities.

- This section shall not apply to any one-story building or structure of an institution or home for the care of the aged providing 24-hour-per-day care if such building or structure is used or intended to be used for the housing of no more than six ambulatory aged persons. Such buildings or institutions shall have installed and maintained in an operable condition herein a fire alarm system of a type approved by the state fire marshal. Such system shall be activated by detectors responding to either visible or invisible particles of combustion other than heat, except that detectors used in closets, usable under-floor areas, storage rooms, bathrooms, attached garages, attics, plenums, laundry rooms and rooms of similar use, may be heat-responsive devices.

- This section shall not apply to occupancies or any alterations thereto conforming to the construction provisions of this exception which were under construction or in existence on March 4, 1972. "Under construction" as used in this exception shall mean that actual work had been performed on the construction site and shall not be construed to mean that the hospital, home, nursery, institution, sanitarium or any portion thereof, was or is in the planning stage. The provisions of this exception shall apply to those buildings or structures having bearing walls and structural frames protected in accordance with the provisions of Column Type IA of Table 601.

- In detention facilities where inmates are not restrained.

The provisions of this section shall not apply to any facility used to house six or less persons on the premises.

407.7.1

When a new addition is to be made to an unsprinklered building or structure as permitted by this subsection, such new addition shall be sprinklered as required by this section and shall be separated from the existing building or structures by not less than a two-hour fire-resistive fire barrier.

When a sprinkler system is added to an existing unsprinklered building or structure, the sprinklered area(s) shall be separated from the remainder of the building by not less than a one-hour fire-resistive fire barrier. The provisions of this section do not apply to any facility used to house six or less persons on the premises.

[F] 407.8 Fire Alarm System

A fire alarm system shall be provided in accordance with Section 907.2.6.

[F] 407.9 Automatic Smoke Detection

Automatic smoke detection shall be provided in accordance with Section 907.2.6.2.2.

Group I-2, Condition 2 occupancies shall be equipped with smoke detection as required in Section 407.2.

Exceptions:

- Corridor smoke detection is not required where sleeping rooms are provided with smoke detectors that comply with UL 268. Such detectors shall provide a visual display on the corridor side of each sleeping room and an audible and visual alarm at the care provider's station attending each unit.

- Corridor smoke detection is not required where sleeping room doors are equipped with automatic door-closing devices with integral smoke detectors on the unit sides installed in accordance with their listing, provided that the integral detectors perform the required alerting function.

[BE] 407.10 Secured Yards

Grounds are permitted to be fenced and gates therein are permitted to be equipped with locks, provided that safe dispersal areas having 30 net square feet (2.8 m2) for bed and stretcher care recipients and 6 net square feet (0.56 m2) for ambulatory care recipients and other occupants are located between the building and the fence. Such provided safe dispersal areas shall be located not less than 50 feet (15 240 mm) from the building they serve. Each safe dispersal area shall have a minimum of two exits. The aggregate clear width of exits from a safe dispersal area shall be determined on the basis of not less than one exit unit of 22 inches (559 mm) for each 500 persons to be accommodated, and no exit shall be less than 44 inches (1118 mm) in width. Gates shall not be installed across corridors or passageways leading to such dispersal areas unless they comply with egress requirements. Keys to gate locks shall be provided in accordance with the California Fire Code.

[F] 407.11 Electrical Systems

In Group I-2 occupancies, electrical construction and installation shall be in accordance with the provisions of Chapter 27, Article 517 of the California Electrical Code and NFPA 99.

407.12 Technology Equipment Center

A technology equipment center serving a Group I-2 occupancy shall be separated from other portions of the building by not less than a 1-hour fire barrier constructed in accordance with Section 707 and a 1-hour horizontal assembly constructed in accordance with Section 711 or both.

407.13 Special Hazards

407.13.1

Storage and handling of flammable, combustible liquids and hazardous materials shall be in accordance with the California Fire Code.

407.13.2

All exterior openings in a boiler room or room containing central heating equipment, if located below openings in another story, or if less than 10 feet (3048 mm) from other doors or windows of the same building, shall be protected by a fire assembly having a three-fourths-hour fire protection rating.

407.13.3 Safety Padding

See Sections 308.1 and 408.14.

407.13.4 Floor Surfaces

Rooms occupied by patients whose personal liberties are restrained shall have noncombustible floor surfaces see Sections 308.1 and 804.4.3.

Section 408 Group I-3

Diagram

UpCodes Diagram (1)

Ships Ladders in Group I-3

408.1 General

Diagram

Occupancies in Group I-3 shall comply with the provisions of Sections 408.1 through 408.11 and other applicable provisions of this code (see Section 308.5).

UpCodes Diagram (1)

Detention & Correctional Facilities - Common Use Areas

408.1.2 Construction

Group I-3 Occupancies shall be housed in buildings of Type IA or Type IB.

Exception: Such occupancies may be housed in one-story buildings of Type IIA, Type IIIA or Type VA construction provided the floor area does not exceed 5,200 square feet (483 m2) between fire walls of two-hour fire-resistive construction with openings protected by fire assemblies having 1- and 11/2-hour fire-protection rating.

408.1.2.1 Nonbearing Walls and Partitions Interior

Nonbearing cell or dormitory walls within cell complexes shall be of noncombustible construction.

408.1.2.2 Intervening Spaces

Common rooms and spaces within Group I-3 occupancies of Type I construction shall be considered an intervening space in accordance with Section 1016.2 when the area is contained within housing units or suites, and not considered a corridor, when they meet any of the following:

- Within prisons and local detention facilities of Type I construction, the exit access within a housing unit may be non-rated provided the required exit occupant load from any dayroom does not exceed 64 persons.

- Within prison, jails and courthouses: Circulation within any temporary holding suite of Type I construction and an occupant load less than 100.

- Within prisons and local detention facilities, correctional medical or mental health housing suites, of Type I construction and an occupant load less than 100.

- Within prisons and local detention facilities of Type I construction, detention program housing units or suites having an occupant load less than 100.

408.1.2.3 Courthouse Holding Facilities

Group I-3 courthouse holding facilities shall be considered a separate and distinct building from the remaining courthouse building for the purpose of determining the type of construction where all of the following conditions are met:

- 2-hour fire barriers in accordance with Section 707 and 2-hour horizontal assemblies in accordance with Section 711 are provided to separate the courthouse holding facility from all other portions of the courthouse building.

- Any of the structure used to support courthouse holding facilities meets the requirements for the Group I-3 portion of the building.

- Each courthouse holding facility located above the first story is less than 1,000 square feet in area, and is designed to hold 10 or less in-custody defendants.

- Courthouse holding facilities located above the first story containing an internal stairway discharging to the main courthouse holding facility at the first story or basement.

- Additional exits from the courthouse holding facility located above the first story shall be permitted to exit through the courtrooms.

- The main courthouse holding facility located on the first story or basement has at least one exit directly to the exterior and additional means of egress shall be permitted to pass through a 1-hour corridor or lobby in the courthouse building.

408.1.2.4 Horizontal Building Separation for Combined Group I-3/Group B Occupancy

A Group B Administration building one story in height shall be permitted to be located above a Group I-3 (or Group I-3/I-2) housing/treatment building that is one story above grade and shall be classified as a separate and distinct building for the purpose of determining the type of construction, and shall be considered a separate fire area, where all of the following conditions are met:

- A 3-hour floor-ceiling assembly below the administration building is constructed as a horizontal assembly in accordance with Section 711.

- Interior shafts for stairs, elevators and mechanical systems complete the 3-hour separation between the Group B and Group I-3 (or Group I-3/I-2).

- The Group I-3 occupancy (or Group I-3/I-2 occupancies, correctional medical and mental health uses) below is minimum Type I-B construction with 2-hour fire resistive rated exterior walls.

- No unprotected openings are allowed in lower roofs within 10 feet of unprotected windows in the upper floor.

- The Group B building above is of noncombustible construction and equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

- The Group B occupancy building above has all required means of egress capable of discharging directly to the exterior to a safe dispersal area.

408.1.2.5 Temporary Holding Area

In buildings protected with automatic sprinklers, corridor serving temporary holding rooms shall be one hour fire resistance rated when the temporary holding occupant load is greater than 20.

408.1.2.6 Temporary Holding Facilities

Temporary holding facilities with nine or fewer persons under restraint may be classified as Group B when located in a buildings complying with all of the following conditions:

- The building shall be protected throughout with a monitored automatic sprinkler system installed in accordance with Section 903.3.1.1.

- The building shall protected with a automatic fire alarm system with notification appliances throughout the holding facility in accordance with Section 907.2.

- The building shall be constructed of Type I, IIA, IIIA or VA construction.

408.1.2.7 Secure Interview Rooms

Secure Interview Rooms used for law enforcement shall be permitted to locked, and shall not be classified as Group I-3 occupancies where all of the following conditions are met:

- A monitored automatic sprinkler system shall be provided throughout buildings and portions thereof including secure interview rooms. The automatic sprinkler system shall comply with Section 903.3.1.1.

- Secure interview rooms shall be located in non-combustible construction.

- Secure interview rooms have glazed or barred openings with direct, continuous observation from law enforcement personnel who have a means to open the secure interview room.

- Not more than 6 occupants in secure interview rooms shall be located in the same fire area.

- An automatic smoke detection system shall be installed within secure interview rooms and mechanical and electrical rooms.

408.1.3 Security Door Assemblies in Corridors, Smoke Barriers and Smoke Partitions

Security door assemblies shall be constructed in accordance with NFPA 252 or UL 10C, and where a smoke rating is required UL 1784, are not required to be tested or labeled.

408.2 Other Occupancies

Buildings or portions of buildings in Group I-3 occupancies where security operations necessitate the locking of required means of egress shall be permitted to be classified as a different occupancy. Occupancies classified as other than Group I-3 shall meet the applicable requirements of this code for that occupancy where provisions are made for the release of occupants at all times.

Means of egress from detention and correctional occupancies that traverse other use areas shall, as a minimum, conform to requirements for detention and correctional occupancies.

Exceptions:

- It is permissible to exit through a horizontal exit into other contiguous occupancies that do not conform to detention and correctional occupancy egress provisions but that do comply with requirements set forth in the appropriate occupancy, as long as the occupancy is not a Group H use.

- Regardless of the provisions of Section 508, laundry areas and kitchens including associated dining areas, where commercial/institutional equipment is used shall be separated from the remainder of the building by construction capable of resisting the passage of smoke.

- For the purpose of occupancy separation only courtroom docks that are directly accessory to courtrooms need not be separated from a courtroom.

408.2.1 Correctional Medical and Mental Health Uses

Where a Group I-3 occupancy occurs in building or portions of buildings, the following Subsections of Sections of 407 shall apply: 407.2.1; 407.2.2; 407.2.3; 407.3.1; 407.3.1.1; 407.4; 407.10.

[BE] 408.3 Means of Egress

Except as modified or as provided for in this section, the means of egress provisions of Chapter 10 shall apply.

[BE] 408.3.1 Door Width

Doors to resident sleeping units shall have a clear width of not less than 28 inches (711 mm).

408.3.1.1

Cell doors shall open outwardly or slide laterally.

[BE] 408.3.2 Sliding Doors

Where doors in a means of egress are of the horizontal-sliding type, the force to slide the door to its fully open position shall be not greater than 50 pounds (220 N) with a perpendicular force against the door of 50 pounds (220 N).

[BE] 408.3.3 Guard Tower Doors

A hatch or trap door not less than 16 square feet (610 m2) in area through the floor and having dimensions of not less than 2 feet (610 mm) in any direction shall be permitted to be used as a portion of the means of egress from guard towers.

[BE] 408.3.4 Spiral Stairways

Diagram

Spiral stairways that conform to the requirements of Section 1011.10 are permitted for access to and between staff locations.

UpCodes Diagram (1)

Spiral Stairways for Small Occupant Loads

[BE] 408.3.5 Ship's Ladders

Diagram

Ship's ladders shall be permitted for egress from control rooms or elevated facility observation rooms in accordance with Section 1011.15.

UpCodes Diagram (1)

Primary

Ships Ladders in Group I-3

Building products (8)

Ship Ladder (60 degrees) - 520A Ship Ladder

O'Keeffe's

Ship Ladder (75 degrees) - 520 Ship Ladder

O'Keeffe's

Ship Ladder with Access to Roof Hatch (60 degrees) - 523A Ship Ladder

O'Keeffe's

Ship Ladder with Access to Roof Hatch (75 degrees) - 523 Ship Ladder

O'Keeffe's

Ship Ladder with Platform (60 degrees) - 521A Ship Ladder

O'Keeffe's

Ship Ladder with Platform (75 degrees) - 521 Ship Ladder

O'Keeffe's

Ship Ladder with Platform and Return (60 degrees) - 522A Ship Ladder

O'Keeffe's

Ship Ladder with Platform and Return (75 degrees) - 522 Ship Ladder

O'Keeffe's

[BE] 408.3.6 Exit Discharge

Exits are permitted to discharge into a fenced or walled courtyard. Enclosed yards or courts shall be of a size to accommodate all occupants, be located not less than 50 feet (15 240 mm) from the building and have an area of not less than 7 square feet (0.65 m2) per person. A gate shall be provided from the safe dispersal area to allow for the necessary relocation of occupants.

408.3.6.1

Exterior fenced enclosures and fenced enclosures utilized for recreational or activity purposes, used for exit termination for more than 20 persons, and which do not provide a safe dispersal area, shall have not less than two exits.

408.3.6.2

Fenced enclosure utilized for recreational or activity purposes only, for more than 49 people, and which do not provide a safe dispersal area, shall be provided with not less than two exits.

408.3.6.3

Fenced enclosures located on roofs of buildings one or more stories in height shall be provided with not less than two exits regardless of occupant load.

408.3.6.4

Fenced enclosures utilized for central control buildings not normally occupied and not accessed by inmates or the general public are permitted to have only one exit from the fenced enclosure. These fenced enclosures shall only be occupied during emergency response conditions by not more than 29 prison staff occupants. Access to the fenced area shall be controlled remotely or at the gate with a key.

[BE] 408.3.7 Sallyports

A sallyport shall be permitted in a means of egress where there are provisions for continuous and unobstructed passage through the sallyport during an emergency egress condition.

[BE] 408.3.8 Interior Exit Stairway and Ramp Construction

Diagram

One interior exit stairway or ramp in each building shall be permitted to have glazing installed in doors and interior walls at each landing level providing access to the interior exit stairway or ramp, provided that the following conditions are met:

- The interior exit stairway or ramp shall not serve more than four floor levels.

- Exit doors shall be not less than 3/4-hour fire door assemblies complying with Section 716.

- The total area of glazing at each floor level shall not exceed 5,000 square inches (3.2 m2) and individual panels of glazing shall not exceed 1,296 square inches (0.84 m2).

- The glazing shall be protected on both sides by an automatic sprinkler system. The sprinkler system shall be designed to wet completely the entire surface of any glazing affected by fire when actuated.

- The glazing shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler system operates.

- Obstructions, such as curtain rods, drapery traverse rods, curtains, drapes or similar materials shall not be installed between the automatic sprinklers and the glazing.

UpCodes Diagram (1)

Exit Access Stairway Enclosures: I-2 and I-3

408.3.8.1

Where the number and arrangement of exits complies with the requirements of Chapter 10, other stairways which occur within the secure area of the detention facility and are not used for required exiting but are used primarily for the movement of inmates and security staff need not extend to the exterior.

408.3.9 Dead-End Balconies

Exit balconies serving cell tiers shall not extend more than 50 feet (15 240 mm) beyond an exit stairway.

408.3.10 Travel Distance

The travel distance may be increased to 300 feet for portions of Group I-3 occupancies open only to staff or where inmates are escorted at all times by staff.

408.3.11 Number of Exits Required

In temporary holding areas of noncombustible construction, a second means of egress is required when the occupant load is greater than 20.

408.3.12 Custody Station

Spaces for custody stations, communications and related clerical areas shall be permitted to be open to, or located within the corridor, provided the required construction along the perimeter of the corridor is maintained. Construction of custody stations or portions of custody stations, within the envelope of the corridor, is not required to be fire-resistance rated. These provisions shall also apply to an enclosed custody station within the corridor.

TABLE 408.3.13—MAXIMUM FLOOR AREA ALLOWANCES FOR I-3 FACILITIESc

| FUNCTION OF SPACE | OCCUPANT LOAD FACTOR |
| --- | --- |
| Detention facilitiesa,b |  |
| Housing pod | Number of beds and staff |
| Refuge area | 6 net |
| Safe disposal area | 7 net |
| Instructional classroom | 20 net |
| Exercise yard or rooms | 50 gross |
| Dorms sleeping area | 50 gross |
| Holding cell | 10 ft2 per person/40 ft2 minimum |
| Bench seating | 18 inches per person |

For SI:1 inch = 25.4 mm, 1 foot = 304.8 mm.

- Temporary holding cells, rooms or areas shall be calculated based on policies and procedures approved by the authority having jurisdiction. See 408.3.11 for number of exits required.

- Program rooms, day rooms and recreational yards which are dedicated to a housing pod or unit are not factored into the total occupant load of the building. Exiting from individual rooms shall meet the egress requirements of Chapter 10.

- Refer to Chapter 10, Section 1004 or elsewhere in the code for specific requirements based on type of detention facility.

[BE] 408.4 Locks

Egress doors are permitted to be locked in accordance with the applicable use condition. Doors from a refuge area to the outside are permitted to be locked with a key in lieu of locking methods described in Section 408.4.1. The keys to unlock the exterior doors shall be available at all times and the locks shall be operable from both sides of the door. Security hardware may be used on any fire-rated door.

[BE] 408.4.1 Remote Release

Remote release of locks on doors in a means of egress shall be provided with reliable means of operation, remote from the resident living areas, to release locks on all required doors. In Occupancy Condition 3 or 4, the arrangement, accessibility and security of the release mechanisms required for egress shall be such that with the minimum available staff at any time, the lock mechanisms are capable of being released within 2 minutes.

Exception: Provisions for remote locking and unlocking of occupied rooms in Occupancy Condition 4 are not required provided that not more than 10 locks are necessary to be unlocked in order to move occupants from one smoke compartment to a refuge area within 3 minutes. The opening of necessary locks shall be accomplished with not more than two separate keys.

[BE] 408.4.2 Power-Operated Doors and Locks

Diagram

Power-operated sliding doors or power-operated locks for swinging doors shall be operable by a manual release mechanism at the door. Emergency power shall be provided for the doors and locks in accordance with Section 2702.

Exceptions:

- Emergency power is not required in facilities with 10 or fewer locks complying with the exception to Section 408.4.1.

- Emergency power is not required where remote mechanical operating releases are provided.

UpCodes Diagram (1)

Automatic Doors: When Required

[BE] 408.4.3 Redundant Operation

Remote release, mechanically operated sliding doors or remote release, mechanically operated locks shall be provided with a mechanically operated release mechanism at each door, and shall be provided with a redundant remote release control.

[BE] 408.4.4 Relock Capability

Doors remotely unlocked under emergency conditions shall not automatically relock when closed unless specific action is taken at the remote location to enable doors to relock.

408.5 Protection of Vertical Openings

Any vertical opening shall be protected by a shaft enclosure in accordance with Section 713, or shall be in accordance with Section 408.5.1.

408.5.1 Floor Openings

The open space in front of a cell tier and connected chases, not exceeding two tiers in height, shall not be considered a vertical shaft and need not meet the fire-resistive shaft enclosure requirements of Section 713.

408.5.2 Shaft Openings in Communicating Floor Levels

Where a floor opening is permitted between communicating floor levels of a housing unit in accordance with Section 408.5.1, plumbing chases serving vertically stacked individual cells contained with the housing unit shall be permitted without a shaft enclosure.

[BE] 408.6 Smoke Barrier

Assembly

Diagram

Occupancies in Group I-3 shall have smoke barriers complying with Sections 408.6 and 709 to divide every story occupied by residents for sleeping, or any other story having an occupant load of 50 or more persons, into not fewer than two smoke compartments.

Exception: Spaces having a direct exit to one of the following, provided that the locking arrangement of the doors involved complies with the requirements for doors at the smoke barrier for the use condition involved:

- A public way.

- A building separated from the resident housing area by a 2-hour fire-resistance-rated assembly or 50 feet (15 240 mm) of open space.

- A secured yard or court having a holding space 50 feet (15 240 mm) from the housing area that provides 6 square feet (0.56 m2) or more of refuge area per occupant, including residents, staff and visitors.

- Holding facility.

UpCodes Diagram (1)

Smoke Partitions vs. Smoke Barriers

Assemblies (18)

12-1.2: 2hr, Wood

30-1.1: 2hr, I-joist

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

6-1.1: 1hr & 2hr, Steel

6-5.1: 2hr Steel

6-4.1: 2hr Steel - Opt. 2 & 3

6-4.1: 2hr Steel - Opt. 1

28-1.1: 2hr, I-joist

14-1.5: 2hr, Wood

Show 8 more

Building products (2)

FF109X 2 Hour UL Fire Rated Recessed Light Cover

Tenmat

GPX® Ballistic

SaftiFirst

[BE] 408.6.1 Smoke Compartments

The number of residents in any smoke compartment shall be not more than 200. The distance of travel to a door in a smoke barrier from any room door required as exit access shall be not greater than 150 feet (45 720 mm). The distance of travel to a door in a smoke barrier from any point in a room shall be not greater than 200 feet (60 960 mm).

Exception: The travel distance may be increased by 50 feet from areas open only to the staff.

[BE] 408.6.2 Refuge Area

Not less than 6 net square feet (0.56 m2) per occupant shall be provided on each side of each smoke barrier for the total number of occupants in adjoining smoke compartments. This space shall be readily available wherever the occupants are moved across the smoke barrier in a fire emergency.

[BE] 408.6.3 Independent Egress

A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originates.

408.7 Security Glazing

In occupancies in Group I-3, windows and doors in 1-hour fire barriers constructed in accordance with Section 707, fire partitions constructed in accordance with Section 708 and smoke barriers constructed in accordance with Section 709 shall be permitted to have security glazing installed provided that the following conditions are met.

- Individual panels of glazing shall not exceed 1,296 square inches (0.84 m2).

- The glazing shall be protected on both sides by an automatic sprinkler system. The sprinkler system shall be designed to, when actuated, wet completely the entire surface of any glazing affected by fire.

- The glazing shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler system operates.

- Obstructions, such as curtain rods, drapery traverse rods, curtains, drapes or similar materials shall not be installed between the automatic sprinklers and the glazing.

Building product (1)

GPX® Ballistic

SaftiFirst

408.8 Subdivision of Resident Housing Areas

Sleeping areas and any contiguous day room, group activity space or other common spaces where residents are housed shall be separated from other spaces in accordance with Sections 408.8.1 through 408.8.4.

408.8.1 Occupancy Conditions 3 and 4

Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the distance of travel from the sleeping area through the common space to the corridor exceeds 50 feet (15 240 mm).

408.8.2 Occupancy Condition 5

Each sleeping area in Occupancy Condition 5 shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the corridor by a smoke-tight partition.

408.8.3 Openings in Room Face

The aggregate area of openings in a solid sleeping room face in Occupancy Conditions 2, 3, 4 and 5 shall not exceed 120 square inches (0.77 m2). The aggregate area shall include all openings including door undercuts, food passes and grilles. Openings shall be not more than 36 inches (914 mm) above the floor. In Occupancy Condition 5, the openings shall be closeable from the room side.

408.8.4 Smoke-Tight Doors

Doors in openings in partitions required to be smoke tight by Section 408.8 shall be substantial doors, of construction that will resist the passage of smoke. Latches and door closers are not required on cell doors.

408.9 Windowless Buildings

For the purposes of this section, a windowless building or portion of a building is one with nonopenable windows, windows not readily breakable or without windows. Windowless buildings shall be provided with an engineered smoke control system to provide a tenable environment for exiting from the smoke compartment in the area of fire origin in accordance with Section 909 for each windowless smoke compartment.

408.9.1 Smoke Venting

The housing portions of windowless buildings containing use conditions 3, 4, 5 or 9 shall be provided with an engineered smoke control system in accordance with Section 909, windows or doors, smoke vents or equivalent means to provide a tenable environment for exiting from the smoke compartment in the area of fire origin. A tenable environment for egress shall be as defined in NFPA 92. If windows, smoke vents or doors are used to meet this section, at least two windows, smoke vents or doors to the exterior must be provided at or above the highest occupied level in each housing pod, and the windows or doors must be operable or readily breakable and arranged to manually vent smoke.

Exceptions:

- Windowless buildings or portions of a building that meet all of the following requirements:

  - Are Type IA or IB construction.

  - Are protected with sprinklers throughout in accordance with Section 903.3.1.1.

  - Include a fire alarm system with smoke detection in accordance with NFPA 72 in the dayroom and/or corridor serving as exit access from the cells, reporting to a 24 hour central control at the institution.

  - Include at least one exit from each housing unit direct to the exterior where smoke will not accumulate or to the exterior through a 1-hour-rated corridor serving only that unit.

  - The building is divided into at least two smoke compartments per Section 408.6.1.

  - As approved by the enforcing agency, an egress analysis shows that inmates can be evacuated within 6 minutes from the smoke compartment of origin 24 hours per day or when inmates are present.

- No venting or smoke control is required when an engineering analysis shows an acceptable safe egress time compared to the onset of untenable conditions within a windowless building or portion of a windowless building and approved by the enforcing agency. (See Section 909.4.)

[F] 408.10 Fire Alarm System

A fire alarm system shall be provided in accordance with Section 907.2.6.3.

[F] 408.11 Automatic Sprinkler System

Group I-3 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6.

408.12 Emergency and Standby Power Systems

Special electrical systems, exit illumination, power installations and alternate on-site electrical supplies shall be provided for every building or portion of a building housing 10 or more inmates in a detention or correctional facility in accordance with the provisions of the California Electrical Code. There shall be a source of emergency power in all detention facilities capable of providing minimal lighting in all housing units, activity areas, corridors, stairs and central control points, and to maintain fire and life safety, security, communications and alarm systems.

408.13 Windows

In security areas within cell complexes sprinklered throughout, the area of glazing in one-hour corridor walls and smoke barrier walls shall not be restricted, provided:

- 1.   All openings are protected by fixed glazing listed and labeled for a fire-protection of at least 3/4 hour; or

- 2.   Fixed security glazing set in noncombustible frames. Shall comply with the minimum requirements of one of the following test standards: ASTM F1915 Grade 3 glass or H.P. White Laboratory, Inc., HPW-TP- 0500.02, Forced Entry Level III.

- 2.   In lieu of the sizes set forth in CBC, the size and area of glazed assemblies shall conform to the following: Windows required to have a three-fourths-hour fire-resistive rating or windows protected by fixed security glazing, as delineated in Items 1 and 2 above, may have an area not greater than 84 square feet (7.8 m2) with neither width nor height exceeding 12 feet (3658 mm).

408.14 Safety Padding

Padding material used on walls, floors and ceilings in Group I and R-2.1 occupancies shall be of an approved type tested in accordance with the procedures established by State Fire Marshal Standard 12-8-100, Room Fire Test for Wall and Ceiling Materials, California Code of Regulations, Title 24, Part 12.

408.15 Small Management Yards

408.15.1 General

The provisions of Sections 408.15.1 through 408.15.5 shall apply to small management yards. Small management yards may be used by a maximum of two occupants at any one time for a maximum of 2 hours per day.

408.15.2 Construction

Small management yards shall be constructed in accordance with all of the following:

- Constructed of Type IB noncombustible materials.

- Fence material shall be noncombustible.

- Have a maximum area of 150 square feet (14 m2).

- Yard area covering shall not exceed 75 square feet (7 m2) or a maximum of 50 percent of the fenced enclosure.

- Electrical lighting or devices of any type shall not be permitted within the yard.

Exception: Low voltage devices dedicated for the operation of toilets.

408.15.3 Fire Protection System Provisions

408.15.3.1 Automatic Sprinkler Systems

An automatic sprinkler system shall be provided in accordance with Section 903.3.1.1.

Exception: Small management yards where a distance of 10 feet (3048 mm) is maintained from all buildings or structures and 4 feet (1220 mm) is maintained from containment fencing.

408.15.3.2 Fire Alarm Systems

An approved fire alarm system shall be provided in accordance with Section 907.

Exception: Small management yards where a distance of 10 feet (3048 mm) is maintained from all buildings or structures and 4 feet (1220 mm) is maintained from containment fencing.

408.15.4 Means of Egress

Except as modified or as provided for in this section, the provisions of Section 408.3 and Chapter 10 shall apply. Small management yards shall comply with all of the following:

- Staff-controlled manual released locks shall be provided.

- Staff escorting inmates to and from small management yards shall be equipped with radios and personal alarms to notify central control in case of a fire.

- The safe dispersal area as defined by Section 1027.5 shall not be reduced due to placement of these yards.

- An exit, remote from the main entrance is required in the containment fencing.

408.15.5 Special Provisions

Inmate exercise clothing and toilet paper tissue shall be the only combustible materials permitted in small management yards.

408.16 Vehicle Sallyports

A 2-hour fire barrier separation is required at vehicle sallyports. Where a sallyport roof is more than 50 percent open to the sky, no fire barrier separation is required. Solid roofs in sallyports shall be sprinklered complying with Section 903.2.6.2.

Section 409 Motion Picture Projection Rooms

409.1 General

The provisions of Sections 409.1 through 409.5 shall apply to rooms in which ribbon-type cellulose acetate or other safety film is utilized in conjunction with electric arc, xenon or other light-source projection equipment that develops hazardous gases, dust or radiation. Where cellulose nitrate film is utilized or stored, such rooms shall comply with NFPA 40.

409.1.1 Projection Room Required

Every motion picture machine projecting film as mentioned within the scope of this section shall be enclosed in a projection room. Appurtenant electrical equipment, such as rheostats, transformers and generators, shall be within the projection room or in an adjacent room of equivalent construction.

409.2 Construction of Projection Rooms

Every projection room shall be of permanent construction consistent with the construction requirements for the type of building in which the projection room is located. Openings are not required to be protected.

The room shall have a floor area of not less than 80 square feet (7.44 m2) for a single machine and not less than 40 square feet (3.7 m2) for each additional machine. Each motion picture projector, floodlight, spotlight or similar piece of equipment shall have a clear working space of not less than 30 inches by 30 inches (762 mm by 762 mm) on each side and at the rear thereof, but only one such space shall be required between two adjacent projectors. The projection room and the rooms appurtenant thereto shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). The aggregate of openings for projection equipment shall not exceed 25 percent of the area of the wall between the projection room and the auditorium. Openings shall be provided with glass or other approved material, so as to close completely the opening.

409.3 Projection Room and Equipment Ventilation

Ventilation shall be provided in accordance with the California Mechanical Code.

409.3.1 Supply Air

Each projection room shall be provided with adequate air supply inlets so arranged as to provide well-distributed air throughout the room. Air inlet ducts shall provide an amount of air equivalent to the amount of air being exhausted by projection equipment. Air is permitted to be taken from the outside; from adjacent spaces within the building, provided that the volume and infiltration rate are sufficient; or from the building air-conditioning system, provided that it is so arranged as to provide sufficient air when other systems are not in operation.

409.3.2 Exhaust Air

Projection rooms are permitted to be exhausted through the lamp exhaust system. The lamp exhaust system shall be positively interconnected with the lamp so that the lamp will not operate unless there is the required airflow. Exhaust air ducts shall terminate at the exterior of the building in such a location that the exhaust air cannot be readily recirculated into any air supply system. The projection room ventilation system is permitted to also serve appurtenant rooms, such as the generator and rewind rooms.

409.3.3 Projection Machines

Each projection machine shall be provided with an exhaust duct that will draw air from each lamp and exhaust it directly to the outside of the building. The lamp exhaust is permitted to serve to exhaust air from the projection room to provide room air circulation. Such ducts shall be of rigid materials, except for a flexible connector approved for the purpose. The projection lamp or projection room exhaust system, or both, is permitted to be combined but shall not be interconnected with any other exhaust or return system, or both, within the building.

409.4 Lighting Control

Provisions shall be made for control of the auditorium lighting and the means of egress lighting systems of theaters from inside the projection room and from not less than one other convenient point in the building.

409.5 Miscellaneous Equipment

Each projection room shall be provided with rewind and film storage facilities.

Section 410 Stages, Platforms and Technical Production Areas

410.1 Applicability

The provisions of Sections 410.1 through 410.6 shall apply to all parts of buildings and structures that contain stages or platforms and similar appurtenances as herein defined.

410.2 Stages

Stage construction shall comply with Sections 410.2.1 through 410.2.7.

410.2.1 Stage Construction

Stages shall be constructed of materials as required for floors for the type of construction of the building in which such stages are located.

Exception: Stages need not be constructed of the same materials as required for the type of construction provided that the construction complies with one of the following:

- Stages of Type IIB or IV construction with a nominal 2-inch (51 mm) wood deck, provided that the stage is separated from other areas in accordance with Section 410.2.4.

- In buildings of Type IIA, IIIA and VA construction, a fire-resistance-rated floor is not required, provided that the space below the stage is equipped with an automatic sprinkler system or fire-extinguishing system in accordance with Section 903 or 904.

- In all types of construction, the finished floor shall be constructed of wood or approved noncombustible materials. Openings through stage floors shall be equipped with tight-fitting, solid wood trap doors with approved safety locks.

410.2.1.1 Stage Height and Area

Stage areas shall be measured to include the entire performance area and adjacent backstage and support areas not separated from the performance area by fire-resistance-rated construction. Stage height shall be measured from the lowest point on the stage floor to the highest point of the underside of the roof or floor deck above the stage.

410.2.2 Technical Production Areas: Galleries, Gridirons and Catwalks

Diagram

Beams designed only for the attachment of portable or fixed theater equipment, gridirons, galleries and catwalks shall be constructed of approved materials consistent with the requirements for the type of construction of the building; and a fire-resistance rating shall not be required. These areas shall not be considered to be floors, stories, mezzanines or levels in applying this code.

Exception: Floors of fly galleries and catwalks shall be constructed of any approved material.

UpCodes Diagram (1)

Guardrail Openings - Exceptions 3 & 4

410.2.3 Exterior Stage Doors

Where protection of openings is required, exterior exit doors shall be protected with fire door assemblies that comply with Section 716. Exterior openings that are located on the stage for means of egress or loading and unloading purposes, and that are likely to be open during occupancy of the theater, shall be constructed with vestibules to prevent air drafts into the auditorium.

410.2.4 Proscenium Wall

Assembly

Where the stage height is greater than 50 feet (15 240 mm), all portions of the stage shall be completely separated from the seating area by a proscenium wall with not less than a 2-hour fire-resistance rating extending continuously from the foundation to the roof.

Exception: Where a stage is located in a building of Type I construction, the proscenium wall is permitted to extend continuously from a minimum 2-hour fire-resistance-rated floor slab of the space containing the stage to the roof or a minimum 2-hour fire-resistance-rated floor deck above.

Assembly (1)

13-1.2: 2hr, Steel Studs

410.2.5 Proscenium Curtain

Where a proscenium wall is required to have a fire-resistance rating, the stage opening shall be provided with a fire curtain complying with NFPA 80, horizontal sliding doors complying with Section 716 having a fire protection rating of not less than 1 hour, or an approved water curtain complying with Section 903.3.1.1 or, in facilities not utilizing the provisions of smoke-protected assembly seating in accordance with Section 1030.6.2, a smoke control system complying with Section 909 or natural ventilation designed to maintain the smoke level not less than 6 feet (1829 mm) above the floor of the means of egress.

410.2.6 Scenery

Combustible materials used in sets and scenery shall be flame resistant in accordance with the provisions set forth in CCR, Title 19, Division 1, Chapter 8, in accordance with Section 806 and the California Fire Code. Foam plastics and materials containing foam plastics shall comply with Section 2603 and the California Fire Code.

410.2.7 Stage Ventilation

Emergency ventilation shall be provided for stages larger than 1,000 square feet (93 m2) in floor area, or with a stage height greater than 50 feet (15 240 mm). Such ventilation shall comply with Section 410.2.7.1 or 410.2.7.2.

410.2.7.1 Roof Vents

Two or more vents constructed to open automatically by approved heat-activated devices and with an aggregate clear opening area of not less than 5 percent of the area of the stage shall be located near the center and above the highest part of the stage area. Supplemental means shall be provided for manual operation of the ventilator. Curbs shall be provided as required for skylights in Section 2610.2. Vents shall be labeled.

[F] 410.2.7.2 Smoke Control

Smoke control in accordance with Section 909 shall be provided to maintain the smoke layer interface not less than 6 feet (1829 mm) above the highest level of the assembly seating or above the top of the proscenium opening where a proscenium wall is provided in compliance with Section 410.2.4.

410.3 Platform Construction

Permanent platforms shall be constructed of materials as required for the type of construction of the building in which the permanent platform is located. Permanent platforms are permitted to be constructed of fire-retardant-treated wood for Types I, II and IV construction where the platforms are not more than 30 inches (762 mm) above the main floor, and not more than one-third of the room floor area and not more than 3,000 square feet (279 m2) in area. Where the space beneath the permanent platform is used for storage or any purpose other than equipment, wiring or plumbing, the floor assembly shall be not less than 1-hour fire-resistance-rated construction. Where the space beneath the permanent platform is used only for equipment, wiring or plumbing, the underside of the permanent platform need not be protected.

410.3.1 Temporary Platforms

Platforms installed for a period of not more than 30 days are permitted to be constructed of any materials permitted by this code. The space between the floor and the platform above shall only be used for plumbing and electrical wiring to platform equipment.

410.4 Dressing and Appurtenant Rooms

Dressing and appurtenant rooms shall comply with Sections 410.4.1 and 410.4.2.

410.4.1 Separation From Stage

The stage shall be separated from dressing rooms, scene docks, property rooms, workshops, storerooms and compartments contiguous to the stage and other parts of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours for stage heights greater than 50 feet (15 240 mm) and not less than 1 hour for stage heights of 50 feet (15 240 mm) or less.

410.4.2 Separation From Each Other

Assembly

Dressing rooms, scene docks, property rooms, workshops, storerooms and compartments contiguous to the stage shall be separated from each other by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

Assemblies (2)

14-1.1: 1hr, Wood Joist

13-1.1: 1hr Steel Studs

[BE] 410.5 Means of Egress

Diagram

Except as modified or as provided for in this section, the provisions of Chapter 10 shall apply.

UpCodes Diagram (1)

Guardrail Openings - Exceptions 3 & 4

[BE] 410.5.1 Arrangement

Where two or more exits or exit access doorways from the stage are required in accordance with Section 1006.2, not fewer than one exit or exit access doorway shall be provided on each side of a stage.

[BE] 410.5.2 Stairway and Ramp Enclosure

Exit access stairways and ramps serving a stage or platform are not required to be enclosed. Exit access stairways and ramps serving technical production areas are not required to be enclosed.

[BE] 410.5.3 Technical Production Areas

Technical production areas shall be provided with means of egress and means of escape in accordance with Sections 410.5.3.1 through 410.5.3.5.

[BE] 410.5.3.1 Number of Means of Egress

Not fewer than one means of egress shall be provided from technical production areas.

[BE] 410.5.3.2 Exit Access Travel Distance

Diagram

The exit access travel distance shall be not greater than 300 feet (91 440 mm) for buildings without an automatic sprinkler system and 400 feet (122 mm) for buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

UpCodes Diagram (1)

Travel Distance Measurement

[BE] 410.5.3.3 Two Means of Egress

Diagram

Where two means of egress are required, the common path of travel shall be not greater than 100 feet (30 480 mm).

Exception: A means of escape to a roof in place of a second means of egress is permitted.

UpCodes Diagram (1)

Common Path of Egress Travel

[BE] 410.5.3.4 Path of Egress Travel

Diagram

The following exit access components are permitted where serving technical production areas:

- Stairways.

- Ramps.

- Spiral stairways.

- Catwalks.

- Alternating tread devices.

- Permanent ladders.

UpCodes Diagrams (2)

Ladders: Where Permitted

Spiral Stairways for Small Occupant Loads

Building products (19)

Heavy Duty Tubular Rail Fixed Access Ladder - 501 Access Ladder

O'Keeffe's

High Parapet Access with Platform and Return - 533 Cage Ladder

O'Keeffe's

Low Parapet Access with Platform and No Return - 533A Cage Ladder

O'Keeffe's

Low Parapet Access with Roofover Rail Extensions - 532 Cage Ladder

O'Keeffe's

Low Parapet with Walk Through Rail Extension - 534 Cage Ladder

O'Keeffe's

Ship Ladder (60 degrees) - 520A Ship Ladder

O'Keeffe's

Ship Ladder (75 degrees) - 520 Ship Ladder

O'Keeffe's

Ship Ladder with Access to Roof Hatch (60 degrees) - 523A Ship Ladder

O'Keeffe's

Ship Ladder with Access to Roof Hatch (75 degrees) - 523 Ship Ladder

O'Keeffe's

Ship Ladder with Platform (60 degrees) - 521A Ship Ladder

O'Keeffe's

Ship Ladder with Platform (75 degrees) - 521 Ship Ladder

O'Keeffe's

Ship Ladder with Platform and Return (60 degrees) - 522A Ship Ladder

O'Keeffe's

Ship Ladder with Platform and Return (75 degrees) - 522 Ship Ladder

O'Keeffe's

Standard Cage Ladder - 531 Cage Ladder

O'Keeffe's

Standard Duty Channel Rail Fixed Access Ladder - 500 Access Ladder

O'Keeffe's

Tubular Rail High Parapet Access Ladder with Platform and Return - 503 Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Platform Only - 503A Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Roofover Rail Extensions - 502 Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Walk Through Rail Extensions - 504 Access Ladder

O'Keeffe's

[BE] 410.5.3.5 Width

The path of egress travel within and from technical support areas shall be not less than 22 inches (559 mm).

[F] 410.6 Automatic Sprinkler System

Stages shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. Sprinklers shall be installed under the roof and gridiron and under all catwalks and galleries over the stage. Sprinklers shall be installed in dressing rooms, performer lounges, shops and storerooms accessory to such stages.

Exceptions:

- Sprinklers are not required under stage areas less than 4 feet (1219 mm) in clear height that are utilized exclusively for storage of tables and chairs, provided that the concealed space is separated from the adjacent spaces by Type X gypsum board not less than 5/8-inch (15.9 mm) in thickness.

- Sprinklers are not required for stages 1,000 square feet (93 m2) or less in area and 50 feet (15 240 mm) or less in height where curtains, scenery or other combustible hangings are not retractable vertically. Combustible hangings shall be limited to a single main curtain, borders, legs and a single backdrop.

- Sprinklers are not required within portable orchestra enclosures on stages.

- Sprinklers are not required under catwalks and galleries where they are permitted to be omitted in accordance with Section 903.3.1.1.

Section 411 Special Amusement Areas

411.1 General

Special amusement areas having an occupant load of 50 or more shall comply with the requirements for the appropriate Group A occupancy and Sections 411.1 through 411.6. Special amusement areas having an occupant load of less than 50 shall comply with the requirements for a Group B occupancy and Sections 411.1 through 411.6.

Exceptions:

- Special amusement areas that are without walls or a roof and constructed to prevent the accumulation of smoke are not required to comply with this section.

- Puzzle rooms provided with a means of egress that is unlocked, readily identifiable and always available are not required to comply with this section.

[F] 411.2 Automatic Sprinkler System

Buildings containing special amusement areas shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. Where the special amusement area is temporary, less than 180 days, the sprinkler water supply shall be of an approved temporary means determined by the authority having jurisdiction.

Exception: Automatic sprinklers are not required where the total floor area of a temporary, less than 180 days, special amusement area is less than 1,000 square feet (93 m2) and the exit access travel distance from any point in the special amusement area to an exit is less than 50 feet (15 240 mm).

[F] 411.3 Detection and Alarm Systems

Buildings containing special amusement areas shall be equipped throughout with an automatic smoke detection system and an emergency voice/alarm communications system in accordance with Section 907. Presignal alarms and alarm activation shall comply with Sections 411.3.1 and 411.3.2. Emergency voice/alarm communications systems shall comply with Section 411.3.3.

[F] 411.3.1 Alarm Presignal

Activation of any single smoke detector, the automatic sprinkler system or any other single automatic fire-detection device shall immediately initiate an audible and visible alarm at a constantly attended location at the special amusement area from which emergency action, including the manual requirements in Section 411.3.2, can be initiated.

[F] 411.3.2 Alarm Activation

Activation of two or more smoke detectors, a single smoke detector equipped with an alarm verification feature, two or more other approved fire detection devices, the automatic sprinkler system, or a manual control located at the constantly attended station required by Section 411.3.1 shall automatically accomplish all of the following:

- Illumination of the means of egress with an illumination level not less than 1 footcandle (11 lux) at the walking surface level.

- Cessation of conflicting or confusing sounds and visual distractions.

- Activation of approved directional exit markings.

- Activation of a prerecorded message, audible throughout the special amusement area, instructing occupants to proceed to the nearest exit. Alarm signals used in conjunction with the prerecorded message shall produce a sound that is distinct from other sounds used during normal operation of the special amusement area.

[F] 411.3.3 Emergency Voice/Alarm Communications System

An emergency voice/alarm communications system complying with Section 907.5.2.2 shall be installed in and audible throughout special amusement areas. The emergency voice/alarm communications system is allowed to also serve as a public address system.

[BE] 411.4 Exit Marking

Exit signs shall be installed at the required exit or exit access doorways serving special amusement areas in accordance with this section and Section 1013. Approved directional exit markings shall be provided. Where mirrors, mazes or other designs disguise the path of egress travel such that the path of egress travel is not apparent, approved and listed low-level exit signs that comply with Section 1013.5, and directional path markings listed in accordance with UL 1994, shall be provided and located not more than 8 inches (203 mm) above the walking surface and on or near the path of egress travel. Such markings shall become visible in an emergency. The directional exit marking shall be activated by the automatic smoke detection system and the automatic sprinkler system in accordance with Section 411.3.2.

[BE] 411.4.1 Photoluminescent Exit Signs

Where photoluminescent exit signs are installed, such signs shall be listed and the activating light source and viewing distance shall be in accordance with the listing and markings on the signs.

411.5 Interior Finish

Interior wall and ceiling finish materials in special amusement areas shall meet the flame spread index and smoke-developed index requirements for Class A in accordance with Section 803.1.

411.6 Flammable Decorative Materials

Flammable decorative materials shall comply with Section 806.

Section 412 Aircraft-Related Occupancies

412.1 General

Aircraft-related occupancies shall comply with Sections 412.1 through 412.7 and the California Fire Code .

412.2 Airport Traffic Control Towers

The provisions of Sections 412.2.1 through 412.2.6 shall apply to airport traffic control towers occupied only for the following uses:

- Airport traffic control cab.

- Electrical and mechanical equipment rooms.

- Airport terminal radar and electronics rooms.

- Office spaces incidental to the tower operation.

- Lounges for employees, including sanitary facilities.

412.2.1 Construction

The construction of airport traffic control towers shall comply with the provisions of Sections 412.2.1.1 through 412.2.1.3.

412.2.1.1 Type of Construction

Airport traffic control towers shall be constructed to comply with the height limitations of Table 412.2.1.1.

TABLE 412.2.1.1—HEIGHT LIMITATIONS FOR AIRPORT TRAFFIC CONTROL TOWERS

| TYPE OF CONSTRUCTION | HEIGHTa (feet) |
| --- | --- |
| IA | Unlimited |
| IB | 240 |
| IIA | 100 |
| IIB | 85 |
| IIIA | 65 |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.

- Height to be measured from grade plane to cab floor.

[BS] 412.2.1.2 Structural Integrity of Interior Exit Stairways and Elevator Hoistway Enclosures

Enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Section 403.2.2 in airport traffic control towers where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access.

[BS] 412.2.1.3 Sprayed Fire-Resistive Materials (SFRM)

The bond strength of the SFRM installed in airport traffic control towers shall be in accordance with Section 403.2.3 where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access.

[BE] 412.2.2 Means of Egress and Evacuation

The means of egress in airport traffic control towers shall comply with Sections 412.2.2.1 through 412.2.2.3.

[BE] 412.2.2.1 Stairways

Stairways in airport traffic control towers shall be in accordance with Section 1011. Exit stairways shall be smokeproof enclosures complying with one of the alternatives provided in Section 909.20.

Exception: Stairways in airport traffic control towers are not required to comply with Section 1011.12.

[BE] 412.2.2.2 Exit Access

From observation levels, airport traffic control towers shall be permitted to have a single means of exit access for a distance of travel not greater than 100 feet (30 480 mm). Exit access stairways from the observation level need not be enclosed.

[BE] 412.2.2.3 Number of Exits

Not less than one exit stairway shall be permitted for airport traffic control towers of any height provided that the occupant load per floor is not greater than 15 and the area per floor does not exceed 1,500 square feet (140 m2).

[BE] 412.2.2.3.1 Interior Finish

Where an airport traffic control tower is provided with only one exit stairway, interior wall and ceiling finishes shall be either Class A or Class B.

[BE] 412.2.2.3.2 Exit Separation

Where an airport traffic control tower is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and two exits are required, the exit separation distance required by Section 1007 shall be not less than one-fourth of the length of the maximum overall dimension of the area served.

[F] 412.2.3 Emergency Systems

The detection, alarm and emergency systems of airport traffic control towers shall comply with Sections 412.2.3.1 through 412.2.3.3.

[F] 412.2.3.1 Automatic Smoke Detection Systems

Airport traffic control towers shall be provided with an automatic smoke detection system installed in accordance with Section 907.2.22.

[F] 412.2.3.2 Fire Command Center

Diagram

A fire command center shall be provided in airport traffic control towers where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access. The fire command center shall comply with Section 911.

Exceptions:

- The fire command center shall be located in the airport control tower or an adjacent contiguous building where building functions are interdependent.

- The room shall be not less than 150 square feet (14 m2) in area with a minimum dimension of 10 feet (3048 mm).

- The following features shall not be required in an airport traffic control tower fire command center.

  - Emergency voice/alarm control unit.

  - Public address system.

  - Status indicators and controls for the air distributions centers.

  - Generator supervision devices, manual start and transfer features.

  - Elevator emergency or standby power switches where emergency or standby power is provided.

UpCodes Diagram (1)

Fire Command Center

[F] 412.2.3.3 Smoke Removal

Smoke removal in airport traffic control towers shall be provided in accordance with Section 403.4.7.

[F] 412.2.4 Automatic Sprinkler System

Where an occupied floor is located more than 35 feet (10 668 mm) above the lowest level of fire department vehicle access, airport traffic control towers shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.

[F] 412.2.4.1 Fire Pump Room

Assembly

Diagram

Fire pumps shall be located in rooms that are separated from all other areas of the building by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both.

Exception: Separation is not required for fire pumps physically separated in accordance with NFPA 20.

UpCodes Diagram (1)

Fire Pump Room Doors

Assembly (1)

13-1.2: 2hr, Steel Studs

[F] 412.2.5 Protection of Elevator Wiring and Cables

Wiring and cables serving elevators in airport traffic control towers shall be protected in accordance with Section 3007.8.1.

[F] 412.2.5.1 Elevators for Occupant Evacuation

Diagram

Where provided in addition to an exit stairway, occupant evacuation elevators shall be in accordance with Section 3008.

UpCodes Diagram (1)

Occupant Evacuation Elevator Lobbies

[BE] 412.2.6 Accessibility

[DSA-AC] In air traffic control towers, an accessible route shall not be required to serve the cab and the equipment areas on the floor immediately below the cab.

412.3 Aircraft Hangars

Diagram

Aircraft hangars shall be in accordance with Sections 412.3.1 through 412.3.6.

UpCodes Diagram (1)

Unlimited Area Aircraft Bldgs.

412.3.1 Exterior Walls

Exterior walls located less than 30 feet (9144 mm) from lot lines or a public way shall have a fire-resistance rating not less than 2 hours.

412.3.2 Basements

Where hangars have basements, floors over basements shall be of Type IA construction and shall be made tight against seepage of water, oil or vapors. There shall not be openings or communication between basements and the hangar. Access to basements shall be from outside only.

412.3.3 Floor Surface

Floors shall be graded and drained to prevent water or fuel from remaining on the floor. Floor drains shall discharge through an oil separator to the sewer or to an outside vented sump.

Exception: Aircraft hangars with individual lease spaces not exceeding 2,000 square feet (186 m2) each in which servicing, repairing or washing is not conducted and fuel is not dispensed shall have floors that are graded toward the door, but shall not require a separator.

412.3.4 Heating Equipment

Assembly

Heating equipment shall be placed in another room separated by 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Entrance shall be from the outside or by means of a vestibule providing a two-doorway separation.

Exceptions:

- Unit heaters and vented infrared radiant heating equipment suspended not less than 10 feet (3048 mm) above the upper surface of wings or engine enclosures of the highest aircraft that are permitted to be housed in the hangar need not be located in a separate room provided that they are mounted not less than 8 feet (2438 mm) above the floor in shops, offices and other sections of the hangar communicating with storage or service areas.

- Entrance to the separated room shall be permitted by a single interior door provided that the sources of ignition in the appliances are not less than 18 inches (457 mm) above the floor.

Assembly (1)

13-1.2: 2hr, Steel Studs

412.3.5 Finishing

The process of "doping," involving use of a volatile flammable solvent, or of painting, shall be carried on in a separate detached building equipped with automatic fire-extinguishing equipment in accordance with Section 903.

[F] 412.3.6 Fire Suppression

Aircraft hangars shall be provided with a fire suppression system designed in accordance with NFPA 409, based on the classification for the hangar given in Table 412.3.6.

Exception: Where a fixed base operator has separate repair facilities on site, Group II hangars operated by a fixed base operator used for storage of transient aircraft only shall have a fire suppression system, but the system is exempt from foam requirements.

[F] TABLE 412.3.6— HANGAR FIRE SUPPRESSION REQUIREMENTSa, b, c

| MAXIMUM SINGLE FIRE AREA (square feet) | TYPE OF CONSTRUCTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | IA | IB | IIA | IIB | IIIA | IIIB | IV | VA | VB |
| ≥ 40,001 | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I |
| 40,000 | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 30,000 | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 20,000 | Group III | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 15,000 | Group III | Group III | Group III | Group II | Group III | Group II | Group III | Group II | Group II |
| 12,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II | Group II |
| 8,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II |
| 5,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group III |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.

- Aircraft hangars with a door height greater than 28 feet shall be provided with fire suppression for a Group I hangar regardless of maximum fire area.

- Groups shall be as classified in accordance with NFPA 409.

- Membrane structures complying with Section 3102 shall be classified as a Group IV hangar.

[F] 412.3.6.1 Hazardous Operations

Any Group III aircraft hangar according to Table 412.3.6 that contains hazardous operations including, but not limited to, the following shall be provided with a Group I or II fire suppression system in accordance with NFPA 409 as applicable:

- Doping.

- Hot work including, but not limited to, welding, torch cutting and torch soldering.

- Fuel transfer.

- Fuel tank repair or maintenance not including defueled tanks in accordance with NFPA 409, inerted tanks or tanks that have never been fueled.

- Spray finishing operations.

- Total fuel capacity of all aircraft within the unsprinklered single fire area in excess of 1,600 gallons (6057 L).

- Total fuel capacity of all aircraft within the maximum single fire area in excess of 7,500 gallons (28 390 L) for a hangar with an automatic sprinkler system in accordance with Section 903.3.1.1.

[F] 412.3.6.2 Separation of Maximum Single Fire Areas

Assembly

Maximum single fire areas established in accordance with hangar classification and construction type in Table 412.3.6 shall be separated by 2-hour fire walls constructed in accordance with Section 706. In determining the maximum single fire area as set forth in Table 412.3.6, ancillary uses that are separated from aircraft servicing areas by a fire barrier of not less than 1 hour, constructed in accordance with Section 707, shall not be included in the area.

Assemblies (2)

4-1.1: Concrete Walls

3-1.1 thru 3-1.4: CMU walls

412.4 Residential Aircraft Hangars

Residential aircraft hangars shall comply with Sections 412.4.1 through 412.4.5.

412.4.1 Fire Separation

A hangar shall not be attached to a dwelling unless separated by a fire barrier having a fire-resistance rating of not less than 1 hour. Such separation shall be continuous from the foundation to the underside of the roof and unpierced except for doors leading to the dwelling unit. Doors into the dwelling unit shall be equipped with self-closing devices and conform to the requirements of Section 716 with a noncombustible raised sill not less than 4 inches (102 mm) in height. Openings from a hangar directly into a room used for sleeping purposes shall not be permitted.

[BE] 412.4.2 Egress

A hangar shall provide two means of egress. One of the doors into the dwelling shall be considered as meeting only one of the two means of egress.

[F] 412.4.3 Smoke Alarms

Smoke alarms shall be provided within the hangar in accordance with Section 907.2.22.

412.4.4 Independent Systems

Electrical, mechanical and plumbing drain, waste and vent (DWV) systems installed within the hangar shall be independent of the systems installed within the dwelling. Building sewer lines shall be permitted to be connected outside the structures.

Exception: Smoke detector wiring and feed for electrical subpanels in the hangar.

412.4.5 Height and Area Limits

Residential aircraft hangars shall be not greater than 2,000 square feet (186 m2) in area and 20 feet (6096 mm) in building height.

[F] 412.5 Aircraft Paint Hangars

Diagram

Aircraft painting operations shall be conducted in an aircraft paint hangar that complies with the provisions of Sections 412.5.1 through 412.5.8. Buildings and structures, or parts thereof, used for the application of flammable finishes shall comply with the applicable provisions of Section 416.

UpCodes Diagrams (2)

Unlimited Area Aircraft Bldgs.

Unlimited Area Paint Hangers

[F] 412.5.1 Occupancy Classification

Aircraft paint hangars shall be classified in accordance with the provisions of Section 307.1. Aircraft paint hangars shall comply with the applicable requirements of this code and the California Fire Code for such occupancy.

412.5.2 Construction

Aircraft paint hangars shall be of Type I or II construction.

[F] 412.5.3 Spray Equipment Cleaning Operations

Spray equipment cleaning operations shall be conducted in a liquid use, dispensing and mixing room.

[F] 412.5.4 Operations

Only those flammable liquids necessary for painting operations shall be permitted in quantities less than the maximum allowable quantities per control area in Table 307.1(1). Spray equipment cleaning operations exceeding the maximum allowable quantities per control area in Table 307.1(1) shall be conducted in a liquid use, dispensing and mixing room.

[F] 412.5.5 Storage

Storage of flammable or combustible liquids exceeding the maximum allowable quantities per control area in Table 307.1(1) shall be in a liquid storage room.

[F] 412.5.6 Fire Suppression

Aircraft paint hangars shall be provided with fire suppression as required by NFPA 409.

[F] 412.5.7 Ventilation

Aircraft paint hangars shall be provided with ventilation as required in the California Mechanical Code.

[F] 412.5.8 Electrical

Electrical equipment and devices within the aircraft paint hangar shall comply with California Electrical Code.

[F] 412.5.8.1 Class I, Division I Hazardous Locations

The area within 10 feet (3048 mm) horizontally from aircraft surfaces and from the floor to 10 feet (3048 mm) above the aircraft surface shall be classified as a Class I, Division I location.

[F] 412.5.8.2 Class I, Division 2 Hazardous Locations

The area horizontally from aircraft surfaces between 10 feet (3048 mm) and 30 feet (9144 mm) and from the floor to 30 feet (9144 mm) above the aircraft surface shall be classified as a Class I, Division 2 location.

[BE] 412.6 Aircraft Manufacturing Facilities

Diagram

In buildings used for the manufacturing of aircraft, exit access travel distances indicated in Section 1017.1 shall be increased in accordance with the following:

- The building shall be of Type I or II construction.

- Exit access travel distance shall not exceed the distances given in Table 412.6.

[BE] TABLE 412.6—AIRCRAFT MANUFACTURING EXIT ACCESS TRAVEL DISTANCE

| HEIGHT (feet)b | MANUFACTURING AREA (square feet)a |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | ≥ 150,000 | ≥ 200,000 | ≥ 250,000 | ≥ 500,000 | ≥ 750,000 | ≥ 1,000,000 |
| ≥ 25 | 400 | 450 | 500 | 500 | 500 | 500 |
| ≥ 50 | 400 | 500 | 600 | 700 | 700 | 700 |
| ≥ 75 | 400 | 500 | 700 | 850 | 1,000 | 1,000 |
| ≥ 100 | 400 | 500 | 750 | 1,000 | 1,250 | 1,500 |

For SI: 1 foot = 304.8 mm.

- Contiguous floor area of the aircraft manufacturing facility having the indicated height.

- Minimum height from finished floor to bottom of ceiling or roof slab or deck.

UpCodes Diagrams (2)

Primary

Aircraft Manuf.: Exit Access Travel Dist.

Example: Exit Access Travel Distance

[BE] 412.6.1 Ancillary Areas

Rooms, areas and spaces ancillary to the primary manufacturing area shall be permitted to egress through such area having a minimum height as indicated in Table 412.6. Exit access travel distance within the ancillary room, area or space shall not exceed that indicated in Table 1017.2 based on the occupancy classification of that ancillary area. Total exit access travel distance shall not exceed that indicated in Table 412.6.

[F] 412.7 Heliports and Helistops

Heliports and helistops shall be permitted to be erected on buildings or other locations where they are constructed in accordance with Sections 412.7.1 through 412.7.5.

[F] 412.7.1 Size

The landing area for helicopters less than 3,500 pounds (1588 kg) shall be not less than 20 feet (6096 mm) in length and width. The landing area shall be surrounded on all sides by a clear area having an average width at roof level of 15 feet (4572 mm), and all widths shall be not less than 5 feet (1524 mm).

[F] 412.7.2 Design

Helicopter landing areas and the supports thereof on the roof of a building shall be noncombustible construction. Landing areas shall be designed to confine any flammable liquid spillage to the landing area itself and provisions shall be made to drain such spillage away from any exit or stairway serving the helicopter landing area or from a structure housing such exit or stairway. For structural design requirements, see Section 1607.6.

[BE] 412.7.3 Means of Egress

The means of egress from heliports and helistops shall comply with the provisions of Chapter 10. Landing areas located on buildings or structures shall have two or more exits or access to exits. For landing areas less than 60 feet (18 288 mm) in length or less than 2,000 square feet (186 m2) in area, the second means of egress is permitted to be a fire escape, alternating tread device or ladder leading to the floor below.

Building products (11)

Heavy Duty Tubular Rail Fixed Access Ladder - 501 Access Ladder

O'Keeffe's

High Parapet Access with Platform and Return - 533 Cage Ladder

O'Keeffe's

Low Parapet Access with Platform and No Return - 533A Cage Ladder

O'Keeffe's

Low Parapet Access with Roofover Rail Extensions - 532 Cage Ladder

O'Keeffe's

Low Parapet with Walk Through Rail Extension - 534 Cage Ladder

O'Keeffe's

Standard Cage Ladder - 531 Cage Ladder

O'Keeffe's

Standard Duty Channel Rail Fixed Access Ladder - 500 Access Ladder

O'Keeffe's

Tubular Rail High Parapet Access Ladder with Platform and Return - 503 Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Platform Only - 503A Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Roofover Rail Extensions - 502 Access Ladder

O'Keeffe's

Tubular Rail Low Parapet Access Ladder with Walk Through Rail Extensions - 504 Access Ladder

O'Keeffe's

[F] 412.7.4 Rooftop Heliports and Helistops

Rooftop heliports and helistops shall comply with NFPA 418.

[F] 412.7.5 Standpipe System

Diagram

In buildings equipped with a standpipe system, the standpipe shall extend to the roof level in accordance with Section 905.3.5.

UpCodes Diagram (1)

Standpipe Types

Section 413 Combustible Storage

413.1 General

High-piled stock or rack storage in any occupancy group shall comply with the California Fire Code .

413.2 Attic, Under-Floor and Concealed Spaces

Diagram

Attic, under-floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required for 1-hour fire-resistance-rated construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 13/4 inches (45 mm) in thickness.

Exception: Neither fire-resistance-rated construction nor opening protectives are required in any of the following locations:

- Areas protected by approved automatic sprinkler systems.

- Group R-3 and U occupancies.

UpCodes Diagram (1)

Primary

Combustible Storage in Attics and Under Floor Spaces

Section 414 Hazardous Materials

[F] 414.1 General

Buildings and structures occupied for the manufacturing, processing, dispensing, use or storage of hazardous materials shall comply with Sections 414.1 through 414.6.

Exception: Exemptions listed in Table 307.1.1 shall not be required to comply with Section 414.

[F] 414.1.1 Other Provisions

Buildings and structures with an occupancy in Group H shall comply with this section and the applicable provisions of Section 415 and the California Fire Code. See Section 453 for Group L occupancies.

[F] 414.1.2 Materials

The safe design of hazardous material occupancies is material dependent. Individual material requirements are found in Sections 307 and 415, the California Mechanical Code and the California Fire Code.

[F] 414.1.2.1 Aerosol Products, Aerosol Cooking Spray Products and Plastic Aerosol 3 Products

Level 2 and 3 aerosol products, aerosol cooking spray products and plastic aerosol 3 products shall be stored and displayed in accordance with the California Fire Code. See Section 311.2 and the California Fire Code for occupancy group requirements.

[F] 414.1.3 Information Required

A report shall be submitted to the building official identifying the maximum expected quantities of hazardous materials to be stored, used in a closed system and used in an open system, and subdivided to separately address hazardous material classification categories based on Tables 307.1(1) and 307.1(2). The methods of protection from such hazards, including but not limited to control areas, fire protection systems and Group H occupancies shall be indicated in the report and on the construction documents. The opinion and report shall be prepared by a qualified person, firm or corporation approved by the building official and provided without charge to the enforcing agency.

For buildings and structures with an occupancy in Group H, separate floor plans shall be submitted identifying the locations of anticipated contents and processes so as to reflect the nature of each occupied portion of every building and structure.

[F] 414.2 Control Areas

Diagram

Control areas shall comply with Sections 414.2.1 through 414.2.5 and the California Fire Code.

UpCodes Diagram (1)

Primary

Hazmat Control Areas

[F] 414.2.1 Construction Requirements

Diagram

Control areas shall be separated from each other by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

UpCodes Diagram (1)

Fire & Smoke: Walls vs. Barriers vs. Partitions

[F] 414.2.2 Percentage of Maximum Allowable Quantities

The percentage of maximum allowable quantities of hazardous materials per control area permitted at each floor level within a building shall be in accordance with Table 414.2.2.

[F] TABLE 414.2.2— DESIGN AND NUMBER OF CONTROL AREAS

| STORY |  | PERCENTAGE OF THE MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREAa | NUMBER OF CONTROL AREAS PER STORY | FIRE-RESISTANCE RATING FOR FIRE BARRIERS IN HOURSb |
| --- | --- | --- | --- | --- |
| Above grade plane | Higher than 9 | 5 | 1 | 2 |
|  | 7—9 | 5 | 2 | 2 |
|  | 6 | 12.5 | 2 | 2 |
|  | 5 | 12.5 | 2 | 2 |
|  | 4 | 12.5 | 2 | 2 |
|  | 3 | 50 | 2 | 1 |
|  | 2 | 75 | 3 | 1 |
|  | 1 | 100 | 4 | 1 |
| Below grade plane | 1 | 75 | 3 | 1 |
|  | 2 | 50 | 2 | 1 |
|  | Lower than 2 | Not Allowed | Not Allowed | Not Allowed |

- Percentages shall be of the maximum allowable quantity per control area shown in Tables 307.1(1) and 307.1(2), with all increases allowed in the notes to those tables.

- Separation shall include fire barriers and horizontal assemblies as necessary to provide separation from other portions of the building.

[F] 414.2.3 Number

Diagram

The maximum number of control areas within a building shall be in accordance with Table 414.2.2. For the purposes of determining the number of control areas within a building, each portion of a building separated by one or more fire walls complying with Section 706 shall be considered a separate building.

UpCodes Diagram (1)

Fire & Smoke: Walls vs. Barriers vs. Partitions

[F] 414.2.4 Fire-Resistance Rating Requirements

Assembly

The required fire-resistance rating for fire barriers shall be in accordance with Table 414.2.2. The floor assembly of the control area and the construction supporting the floor of the control area shall have a fire-resistance rating of not less than 2 hours.

Exception: The floor assembly of the control area and the construction supporting the floor of the control area are allowed to be 1-hour fire-resistance-rated in buildings of Types IIA, IIIA, IV and VA construction, provided that both of the following conditions exist:

- The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

- The building is three or fewer stories above grade plane.

Assemblies (22)

12-1.2: 2hr, Wood

6-1.2: 1hr & 2hr, Solid Gyp Plaster

6-2.2: 1hr & 2hr, Solid Gyp

27-1.1: 1hr, I-joist

30-1.1: 2hr, I-joist

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

6-1.1: 1hr & 2hr, Steel

6-5.1: 2hr Steel

6-4.1: 2hr Steel - Opt. 2 & 3

Show 12 more

Building product (1)

FF109X 2 Hour UL Fire Rated Recessed Light Cover

Tenmat

[F] 414.2.5 Hazardous Material in Group M Display and Storage Areas and in Group S Storage Areas

Diagram

Hazardous materials located in Group M and Group S occupancies shall be in accordance with Sections 414.2.5.1 through 414.2.5.4.

UpCodes Diagram (1)

Primary

Hazmat in Group M (2024)

[F] 414.2.5.1 Nonflammable Solids and Nonflammable and Noncombustible Liquids

The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials permitted within a single control area of a Group M display and storage area, a Group S storage area or an outdoor control area is permitted to exceed the maximum allowable quantities per control area specified in Tables 307.1(1) and 307.1(2) without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with the California Fire Code and quantities do not exceed the maximum allowable specified in Table 414.2.5.1.

[F] TABLE 414.2.5.1— MAXIMUM ALLOWABLE QUANTITY PER INDOOR AND OUTDOOR CONTROL AREA IN GROUP M AND S OCCUPANCIES OF NONFLAMMABLE SOLIDS AND NONFLAMMABLE AND NONCOMBUSTIBLE LIQUIDSd, e, f

| CONDITION |  | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA |  |
| --- | --- | --- | --- |
| Materiala | Class | Solids (pounds) | Liquids (gallons) |
| A. Health-hazard materials—nonflammable and noncombustible solids and liquids |  |  |  |
| 1. Corrosivesb, c | Not Applicable | 9,750 | 975 |
| 2. Highly toxics | Not Applicable | 20b, c | 2b, c |
| 3. Toxicsb, c | Not Applicable | 1,000k | 100 |
| B. Physical-hazard materials—nonflammable and noncombustible solids and liquids |  |  |  |
| 1. Oxidizersb, c | 4 | Not Allowed | Not Allowed |
|  | 3 | 1500g | 150 |
|  | 2 | 2,250h | 225 |
|  | 1 | 18,000i, j | 1,800i, j |
| 2. Unstable (reactives)b, c | 4 | Not Allowed | Not Allowed |
|  | 3 | 550 | 55 |
|  | 2 | 1,150 | 115 |
|  | 1 | Not Limited | Not Limited |
| 3. Water reactives | 3b, c | 550 | 55 |
|  | 2b, c | 1,150 | 115 |
|  | 1 | Not Limited | Not Limited |

For SI: 1 pound = 0.454 kg, 1 gallon = 3.785 L.

- Hazard categories are as specified in the California Fire Code.

- Maximum allowable quantities shall be increased 100 percent in buildings that are sprinklered in accordance with Section 903.3.1.1. Where Note c also applies, the increase for both notes shall be applied accumulatively.

- Maximum allowable quantities shall be increased 100 percent where stored in approved storage cabinets, in accordance with the California Fire Code. Where Note b also applies, the increase for both notes shall be applied accumulatively.

- See Table 414.2.2 for design and number of control areas.

- Allowable quantities for other hazardous material categories shall be in accordance with Section 307.

- Maximum quantities shall be increased 100 percent in outdoor control areas.

- Maximum amounts shall be increased to 2,250 pounds where individual packages are in the original sealed containers from the manufacturer or packager and do not exceed 10 pounds each.

- Maximum amounts shall be increased to 4,500 pounds where individual packages are in the original sealed containers from the manufacturer or packager and do not exceed 10 pounds each.

- The permitted quantities shall not be limited in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

- Quantities are unlimited in an outdoor control area.

- Maximum allowable quantities of consumer products shall be increased to 10,000 pounds where individual packages are in the original, sealed containers from the manufacturer and the toxic classification is exclusively based on the LC threshold and no other hazardous materials classifications apply.

[F] 414.2.5.2 Flammable and Combustible Liquids

In Group M occupancy wholesale and retail sales uses, indoor storage of flammable and combustible liquids shall not exceed the maximum allowable quantities per control area as indicated in Table 414.2.5.2, provided that the materials are displayed and stored in accordance with the California Fire Code.

[F] TABLE 414.2.5.2— MAXIMUM ALLOWABLE QUANTITY OF FLAMMABLE AND COMBUSTIBLE LIQUIDS IN WHOLESALE AND RETAIL SALES OCCUPANCIES PER CONTROL AREAa

| TYPE OF LIQUID | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA (gallons) |  |  |
| --- | --- | --- | --- |
|  | Sprinklered in accordance with Note b densities and arrangements | Sprinklered in accordance with Tables 5704.3.6.3(4) through 5704.3.6.3(8) and 5704.3.7.5.1 of the California Fire Code | Nonsprinklered |
| Class IA | 60 | 60 | 30 |
| Class IB, IC, II and IIIA | 7,500c | 15,000c | 1,600 |
| Class IIIB | Unlimited | Unlimited | 13,200 |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2, 1 gallon = 3.785 L, 1 gallon per minute per square foot = 40.75 L/min/m2.

- Control areas shall be separated from each other by not less than a 1-hour fire barrier wall.

- To be considered as sprinklered, a building shall be equipped throughout with an approved automatic sprinkler system with a design providing minimum densities as follows:

  - For uncartoned commodities on shelves 6 feet or less in height where the ceiling height does not exceed 18 feet, quantities are those permitted with a minimum sprinkler design density of Ordinary Hazard Group 2.

  - For cartoned, palletized or racked commodities where storage is 4 feet 6 inches or less in height and where the ceiling height does not exceed 18 feet, quantities are those permitted with a minimum sprinkler design density of 0.21 gallon per minute per square foot over the most remote 1,500-square-foot area.

- Where wholesale and retail sales or storage areas exceed 50,000 square feet in area, the maximum allowable quantities are allowed to be increased by 2 percent for each 1,000 square feet of area in excess of 50,000 square feet, up to not more than 100 percent of the table amounts. A control area separation is not required. The cumulative amounts, including amounts attained by having an additional control area, shall not exceed 30,000 gallons.

[F] 414.2.5.3 Aerosol Products, Aerosol Cooking Spray Products or Plastic Aerosol 3 Products

The maximum quantity of aerosol products, aerosol cooking spray products or plastic aerosol 3 products in Group M occupancy retail display areas, storage areas adjacent to retail display areas and retail storage areas shall be in accordance with the California Fire Code.

[F] 414.2.5.4 Flammable Gas

The aggregate quantity of Category 1B flammable gas having a burning velocity of 3.9 inches per second (10 cm/s) or less stored and displayed within a single control area of a Group M occupancy or stored in a single control area of a Group S occupancy is allowed to exceed the maximum allowable quantities per control area specified in Table 307.1(1) without classifying the building or use as a Group H occupancy, provided that the materials are stored and displayed in accordance with the California Fire Code and quantities do not exceed the amounts specified in Table 414.2.5.4.

[F] TABLE 414.2.5.4— MAXIMUM ALLOWABLE QUANTITY OF LOW BURNING VELOCITY CATEGORY 1B FLAMMABLE GAS IN GROUP M AND S OCCUPANCIES PER CONTROL AREAa

| CATEGORY 1B (Low BV)d | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA |  |
| --- | --- | --- |
|  | Sprinkleredb | Non-sprinklered |
| Gaseous | 390,000 cu ft | 195,000 cu ft |
| Liquefied | 40,000 lbc | 20,000 lb |

For SI: 1 pound = 0.454 kg, 1 square foot = 0.0929 m2, 1 cubic foot = 0.028 m3, 1 inch per second = 2.54 cm/s.

- Control areas shall be separated from each other by not less than a 1-hour fire barrier.

- The building shall be equipped throughout with an approved automatic sprinkler system with a minimum sprinkler design density of Ordinary Hazard Group 2 in the area where flammable gases are stored or displayed.

- Where storage areas exceed 50,000 square feet in area, the maximum allowable quantities area is allowed to be increased by 2 percent for each 1,000 square feet of area in excess of 50,000 square feet, up to not more than 100 percent of the table amounts. Separation of control areas is not required. The aggregate amount shall not exceed 80,000 pounds.

- Low Burning Velocity (Low BV) Category 1B flammable gas has a burning velocity of 3.9 in/s or less.

[F] 414.3 Ventilation

Rooms, areas or spaces in which explosive, corrosive, combustible, flammable or highly toxic dusts, mists, fumes, vapors or gases are or have the potential to be emitted due to the processing, use, handling or storage of materials shall be mechanically ventilated where required by this code, the California Fire Code or the California Mechanical Code.

Emissions generated at workstations shall be confined to the area in which they are generated as specified in the California Fire Code and the California Mechanical Code.

[F] 414.4 Hazardous Material Systems

Systems involving hazardous materials shall be suitable for the intended application. Controls shall be designed to prevent materials from entering or leaving process or reaction systems at other than the intended time, rate or path. Automatic controls, where provided, shall be designed to be fail safe.

[F] 414.5 Inside Storage, Dispensing, Handling and Use

The inside storage, dispensing and use of hazardous materials shall be in accordance with Sections 414.5.1 through 414.5.3 of this code and the California Fire Code.

[F] 414.5.1 Explosion Control

Explosion control shall be provided in accordance with the California Fire Code as required by Table 414.5.1 where quantities of hazardous materials specified in that table exceed the maximum allowable quantities in Table 307.1(1) or where a structure, room or space is occupied for purposes involving explosion hazards as required by Section 415 or the California Fire Code.

[F] TABLE 414.5.1— EXPLOSION CONTROL REQUIREMENTSa, h

| MATERIAL | CLASS | EXPLOSION CONTROL METHODS |  |
| --- | --- | --- | --- |
|  |  | Barricade construction | Explosion (deflagration) venting or explosion (deflagration) prevention systemsb |
| HAZARD CATEGORY |  |  |  |
| Combustible dustsc | — | Not Required | Required |
| Cryogenic flammables | — | Not Required | Required |
| Explosives | Division 1.1 | Required | Not Required |
|  | Division 1.2 | Required | Not Required |
|  | Division 1.3 | Not Required | Required |
|  | Division 1.4j | Not Required | Required |
|  | Division 1.5 | Required | Not Required |
|  | Division 1.6 | Required | Not Required |
| Flammable gas | Gaseous | Not Required | Requiredk |
|  | Liquefied | Not Required | Requiredk |
| Flammable liquid | IAd | Not Required | Required |
|  | IBe | Not Required | Required |
| Organic peroxides | U | Required | Not Permitted |
|  | I | Required | Not Permitted |
| Oxidizer liquids and solids | 4 | Required | Not Permitted |
| Pyrophoric gas | — | Not Required | Required |
| Unstable (reactive) | 4 | Required | Not Permitted |
|  | 3 Detonable | Required | Not Permitted |
|  | 3 Nondetonable | Not Required | Required |
| Water-reactive liquids and solids | 3 | Not Required | Required |
|  | 2g | Not Required | Required |
| SPECIAL USES |  |  |  |
| Acetylene generator rooms | — | Not Required | Required |
| Electrochemical energy storage systemi | — | Not Required | Required |
| Energy storage systemi | — | Not Required | Required |
| Grain processing | — | Not Required | Required |
| Liquefied petroleum gas-distribution facilities | — | Not Required | Required |
| Where explosion hazards existf | Detonation | Required | Not Permitted |
|  | Deflagration | Not Required | Required |

- See Section 414.1.3.

- See the California Fire Code.

- Combustible dusts where manufactured, generated or used in such a manner that the concentration and conditions create a fire or explosion hazard based on information prepared in accordance with Section 104.2.2 of the California Fire Code. See definition of "Combustible dust" in Chapter 2.

- Storage or use.

- In open use or dispensing.

- Rooms containing dispensing and use of hazardous materials where an explosive environment can occur because of the characteristics or nature of the hazardous materials or as a result of the dispensing or use process.

- A method of explosion control shall be provided where Class 2 water-reactive materials can form potentially explosive mixtures.

- Explosion venting is not required for Group H-5 fabrication areas complying with Section 415.11.1 and the California Fire Code.

- Where explosion control is required in Section 1207 of the California Fire Code.

- Does not apply to consumer fireworks, Division 1.4G.

- Not required for Category 1B Flammable Gases having a burning velocity not exceeding 3.9 inches per second (10 cm/s).

[F] 414.5.2 Emergency or Standby Power

Diagram

Where required by the California Fire Code or this code, mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems shall be provided with emergency or standby power in accordance with Section 2702. For storage and use areas for highly toxic or toxic materials, see Sections 6004.2.2.8 and 6004.3.4.2 of the California Fire Code.

UpCodes Diagram (1)

Standby Power Systems

[F] 414.5.2.1 Exempt Applications

Emergency or standby power is not required for the mechanical ventilation systems provided for any of the following:

- Storage of Class IB and IC flammable and combustible liquids in closed containers not exceeding 6.5 gallons (25 L) capacity.

- Storage of Class 1 and 2 oxidizers.

- Storage of Class II, III, IV and V organic peroxides.

- Storage of asphyxiant, irritant and radioactive gases.

[F] 414.5.2.2 Fail-Safe Engineered Systems

Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed.

[F] 414.5.3 Spill Control, Drainage and Containment

Rooms, buildings or areas occupied for the storage of solid and liquid hazardous materials shall be provided with a means to control spillage and to contain or drain off spillage and fire protection water discharged in the storage area where required in the California Fire Code. The methods of spill control shall be in accordance with the California Fire Code.

414.5.4 Hazardous Material Handling

The handling of hazardous materials shall be in accordance with California Fire Code Section 5003.

[F] 414.6 Outdoor Storage, Dispensing and Use

The outdoor storage, dispensing and use of hazardous materials shall be in accordance with the California Fire Code.

[F] 414.6.1 Weather Protection

Where weather protection is provided for sheltering outdoor hazardous material storage or use areas, such areas shall be considered outdoor storage or use where the weather protection structure complies with Sections 414.6.1.1 through 414.6.1.3.

[F] 414.6.1.1 Walls

Walls shall not obstruct more than one side of the structure.

Exception: Walls shall be permitted to obstruct portions of multiple sides of the structure, provided that the obstructed area is not greater than 25 percent of the structure's perimeter.

[F] 414.6.1.2 Separation Distance

The distance from the structure to buildings, lot lines, public ways or means of egress to a public way shall be not less than the distance required for an outside hazardous material storage or use area without weather protection.

[F] 414.6.1.3 Noncombustible Construction

The overhead structure shall be of approved noncombustible construction with a maximum area of 1,500 square feet (140 m2).

Exception: The maximum area is permitted to be increased as provided by Section 506.

Section 415 Groups H-1, H-2, H-3, H-4 and H-5

[F] 415.1 General

Occupancies classified as Group H-1, H-2, H-3, H-4 and H-5 in accordance with Section 307 shall comply with Sections 415.1 through 415.11.

[F] 415.2 Compliance

Buildings and structures with an occupancy in Group H shall comply with the applicable provisions of Section 414 and the California Fire Code.

[F] 415.3 Automatic Fire Detection Systems

Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2.

[F] 415.4 Automatic Sprinkler System

Group H occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5.

[F] 415.5 Emergency Alarms

Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided as set forth herein.

[F] 415.5.1 Storage

An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials.

[F] 415.5.2 Dispensing, Use and Handling

Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors, interior exit stairways or ramps, or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, proprietary or remote station service or constantly attended on-site location and shall initiate a local audible alarm.

[F] 415.5.3 Supervision

Emergency alarm systems required by Section 415.5.1 or 415.5.2 shall be electrically supervised and monitored by an approved central, proprietary or remote station service or shall initiate an audible and visual signal at a constantly attended on-site location.

[F] 415.5.4 Emergency Alarm Systems

Emergency alarm systems required by Section 415.5.1 or 415.5.2 shall be provided with emergency or standby power in accordance with Section 2702.2.

[F] 415.6 Fire Separation Distance

Diagram

Group H occupancies shall be located on property in accordance with the other provisions of this chapter. In Groups H-2 and H-3, not less than 25 percent of the perimeter wall of the occupancy shall be an exterior wall.

UpCodes Diagram (1)

Primary

Unlimited Area Exception: Group H

[F] 415.6.1 Rooms for Flammable or Combustible Liquid Use, Dispensing or Mixing in Open Systems

Rooms for flammable or combustible liquid use, dispensing or mixing in open systems having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the California Fire Code and NFPA 30.

[F] 415.6.2 Liquid Storage Rooms and Rooms for Flammable or Combustible Liquid Use in Closed Systems

Liquid storage rooms and rooms for flammable or combustible liquid use in closed systems, having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the California Fire Code and NFPA 30.

[F] 415.6.3 Spray Paint Booths

Spray paint booths that comply with the California Fire Code need not be located on the outer perimeter.

[F] 415.6.4 Group H Occupancy Minimum Fire Separation Distance

Diagram

Regardless of any other provisions, buildings containing Group H occupancies shall be set back to the minimum fire separation distance as set forth in Sections 415.6.4.1 through 415.6.4.4. Distances shall be measured from the walls enclosing the occupancy to lot lines, including those on a public way. Distances to assumed lot lines established for the purpose of determining exterior wall and opening protection are not to be used to establish the minimum fire separation distance for buildings on sites where explosives are manufactured or used where separation is provided in accordance with the quantity distance tables specified for explosive materials in the California Fire Code.

UpCodes Diagram (1)

Primary

Fire Separation Distance: Group H

[F] 415.6.4.1 Group H-1

Group H-1 occupancies shall be set back not less than 75 feet (22 860 mm) and not less than required by the California Fire Code.

Exception: Fireworks manufacturing buildings separated in accordance with NFPA 1124.

[F] 415.6.4.2 Group H-2

Group H-2 occupancies shall be set back not less than 30 feet (9144 mm) where the area of the occupancy is greater than 1,000 square feet (93 m2) and it is not required to be located in a detached building.

[F] 415.6.4.3 Groups H-2 and H-3

Group H-2 and H-3 occupancies shall be set back not less than 50 feet (15 240 mm) where a detached building is required (see Table 415.6.5).

[F] 415.6.4.4 Explosive Materials

Group H-2 and H-3 occupancies containing materials with explosive characteristics shall be separated as required by the California Fire Code. Where separations are not specified, the distances required shall be determined by a technical report issued in accordance with Section 414.1.3.

[F] 415.6.5 Detached Buildings for Group H-1, H-2 or H-3 Occupancy

The storage or use of hazardous materials in excess of those amounts specified in Table 415.6.5 shall be in accordance with the applicable provisions of Sections 415.7 and 415.8.

[F] TABLE 415.6.5— DETACHED BUILDING REQUIRED

| A DETACHED BUILDING IS REQUIRED WHERE THE QUANTITY OF MATERIAL EXCEEDS THAT SPECIFIED HEREIN |  |  |  |
| --- | --- | --- | --- |
| Material | Class | Solids and Liquids (tons)a, b | Gases (cubic feet)a, b |
| Explosives | Division 1.1 | Maximum Allowable Quantity | Not Applicable |
|  | Division 1.2 | Maximum Allowable Quantity |  |
|  | Division 1.3 | Maximum Allowable Quantity |  |
|  | Division 1.4e | Maximum Allowable Quantity |  |
|  | Division 1.4c, e | 1 |  |
|  | Division 1.5 | Maximum Allowable Quantity |  |
|  | Division 1.6 | Maximum Allowable Quantity |  |
| Oxidizers | Class 4 | Maximum Allowable Quantity | Maximum Allowable Quantity |
| Unstable (reactives) detonable | Class 3 or 4 | Maximum Allowable Quantity | Maximum Allowable Quantity |
| Oxidizer, liquids and solids | Class 3 | 1,200 | Not Applicable |
|  | Class 2 | 2,000 | Not Applicable |
| Organic peroxides | Detonable | Maximum Allowable Quantity | Not Applicable |
|  | Class I | Maximum Allowable Quantity | Not Applicable |
|  | Class II | 25 | Not Applicable |
|  | Class III | 50 | Not Applicable |
| Unstable (reactives) nondetonable | Class 3 | 1 | 2,000 |
|  | Class 2 | 25 | 10,000 |
| Water reactives | Class 3 | 1 | Not Applicable |
|  | Class 2 | 25 | Not Applicable |
| Pyrophoric gasesd | Not Applicable | Not Applicable | 2,000 |

For SI: 1 ton = 906 kg, 1 cubic foot = 0.02832 m3, 1 pound = 0.454 kg.

- For materials that are detonable, the distance to other buildings or lot lines shall be in accordance with Section 415.6 of this code or Chapter 56 of the California Fire Code based on trinitrotoluene (TNT) equivalence of the material, whichever is greater.

- "Maximum Allowable Quantity" means the maximum allowable quantity per control area set forth in Table 307.1(1).

- Limited to Division 1.4 materials and articles, including articles packaged for shipment, that are not regulated as an explosive under Bureau of Alcohol, Tobacco, Firearms and Explosives (BATF) regulations or unpackaged articles used in process operations that do not propagate a detonation or deflagration between articles, provided that the net explosive weight of individual articles does not exceed 1 pound.

- Detached buildings are not required, for gases in gas rooms that support H-5 fabrication facilities where the gas room is separated from other areas by a fire barrier with a fire-resistance rating of not less than 2 hours and the gas is located in a gas cabinet that is internally sprinklered, equipped with continuous leak detection, automatic shutdown and is not manifolded upstream of pressure controls. Additionally, the gas supply is limited to cylinders that do not exceed 125 pounds (57 kg) water capacity in accordance with 49 CFR 173.192 for Hazard Zone A toxic gases.

- Does not apply to consumer fireworks, Division 1.4G.

[F] 415.6.5.1 Wall and Opening Protection

Where a detached building is required by Table 415.6.5, wall and opening protection based on fire separation distance is not required.

[F] 415.7 Special Provisions for Group H-1 Occupancies

Group H-1 occupancies shall be in detached buildings not used for other purposes. Roofs shall be of lightweight construction with suitable thermal insulation to prevent sensitive material from reaching its decomposition temperature. Group H-1 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for both Group H-1 and H-4 occupancies.

[F] 415.7.1 Floors in Storage Rooms

Floors in storage areas for organic peroxides, pyrophoric materials and unstable (reactive) materials shall be of liquid-tight, noncombustible construction.

[F] 415.8 Special Provisions for Group H-2 and H-3 Occupancies

Group H-2 and H-3 occupancies containing quantities of hazardous materials in excess of those set forth in Table 415.6.5 shall be in detached buildings used for manufacturing, processing, dispensing, use or storage of hazardous materials. Materials specified for Group H-1 occupancies in Section 307.3 are permitted to be located within Group H-2 or H-3 detached buildings provided that the amount of materials per control area do not exceed the maximum allowed quantity specified in Table 307.1(1).

[F] 415.8.1 Multiple Hazards

Group H-2 or H-3 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for Group H-2, H-3 or H-4 occupancies as applicable.

[F] 415.8.2 Separation of Incompatible Materials

Hazardous materials other than those specified in Table 415.6.5 shall be allowed in manufacturing, processing, dispensing, use or storage areas when separated from incompatible materials in accordance with the provisions of the California Fire Code.

[F] 415.8.3 Water Reactives

Group H-2 and H-3 occupancies containing water-reactive materials shall be resistant to water penetration. Piping for conveying liquids shall not be over or through areas containing water reactives, unless isolated by approved liquid-tight construction.

Exception: Fire protection piping shall be permitted over or through areas containing water reactives without isolating it with liquid-tight construction.

[F] 415.8.4 Floors in Storage Rooms

Floors in storage areas for organic peroxides, oxidizers, pyrophoric materials, unstable (reactive) materials and water-reactive solids and liquids shall be of liquid-tight, noncombustible construction.

[F] 415.8.5 Waterproof Room

Rooms or areas used for the storage of water-reactive solids and liquids shall be constructed in a manner that resists the penetration of water through the use of waterproof materials. Piping carrying water for other than approved automatic sprinkler systems shall not be within such rooms or areas.

[F] 415.9 Group H-2

Occupancies in Group H-2 shall be constructed in accordance with Sections 415.9.1 through 415.9.3 and the California Fire Code.

[F] 415.9.1 Flammable and Combustible Liquids

The storage, handling, processing and transporting of flammable and combustible liquids in Group H-2 and H-3 occupancies shall be in accordance with Sections 415.9.1.1 through 415.9.1.9, the California Mechanical Code and the California Fire Code.

[F] 415.9.1.1 Mixed Occupancies

Where the storage tank area is located in a building of two or more occupancies and the quantity of liquid exceeds the maximum allowable quantity for one control area, the use shall be completely separated from adjacent occupancies in accordance with the requirements of Section 508.4.

[F] 415.9.1.1.1 Height Exception

Where storage tanks are located within a building not more than one story above grade plane, the height limitation of Section 504 shall not apply for Group H.

[F] 415.9.1.2 Tank Protection

Storage tanks shall be noncombustible and protected from physical damage. Fire barriers or horizontal assemblies or both around the storage tanks shall be permitted as the method of protection from physical damage.

[F] 415.9.1.3 Tanks

Storage tanks shall be approved tanks conforming to the requirements of the California Fire Code.

[F] 415.9.1.4 Leakage Containment

A liquid-tight containment area compatible with the stored liquid shall be provided. The method of spill control, drainage control and secondary containment shall be in accordance with the California Fire Code.

Exception: Rooms where only double-wall storage tanks conforming to Section 415.9.1.3 are used to store Class I, II and IIIA flammable and combustible liquids shall not be required to have a leakage containment area.

[F] 415.9.1.5 Leakage Alarm

An approved automatic alarm shall be provided to indicate a leak in a storage tank and room. The alarm shall sound an audible signal, 15 dBa above the ambient sound level, at every point of entry into the room in which the leaking storage tank is located. An approved sign shall be posted on every entry door to the tank storage room indicating the potential hazard of the interior room environment, or the sign shall state, "WARNING, WHEN ALARM SOUNDS, THE ENVIRONMENT WITHIN THE ROOM MAY BE HAZARDOUS." The leakage alarm shall be supervised in accordance with Chapter 9 to transmit a trouble signal.

[F] 415.9.1.6 Tank Vent

Storage tank vents for Class I, II or IIIA liquids shall terminate to the outdoor air in accordance with the California Fire Code.

[F] 415.9.1.7 Room Ventilation

Storage tank areas storing Class I, II or IIIA liquids shall be provided with mechanical ventilation. The mechanical ventilation system shall be in accordance with the California Mechanical Code and the California Fire Code.

[F] 415.9.1.8 Explosion Venting

Where Class I liquids are being stored, explosion venting shall be provided in accordance with the California Fire Code.

[F] 415.9.1.9 Tank Openings Other Than Vents

Tank openings other than vents from tanks inside buildings shall be designed to ensure that liquids or vapor concentrations are not released inside the building.

[F] 415.9.2 Liquefied Petroleum Gas Facilities

The construction and installation of liquefied petroleum gas facilities shall be in accordance with the requirements of this code, the California Fire Code, the California Plumbing Code, the California Mechanical Code and NFPA 58.

[F] 415.9.3 Dry Cleaning Plants

The construction and installation of dry cleaning plants shall be in accordance with the requirements of this code, the California Mechanical Code, the California Plumbing Code and NFPA 32. Dry cleaning solvents and systems shall be classified in accordance with the California Fire Code.

[F] 415.10 Groups H-3 and H-4

Groups H-3 and H-4 shall be constructed in accordance with the applicable provisions of this code and the California Fire Code.

[F] 415.10.1 Flammable and Combustible Liquids

The storage, handling, processing and transporting of flammable and combustible liquids in Group H-3 occupancies shall be in accordance with Section 415.9.1.

[F] 415.10.2 Gas Rooms

Assembly

Where gas rooms are provided, such rooms shall be separated from other areas by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

Assemblies (2)

14-1.1: 1hr, Wood Joist

13-1.1: 1hr Steel Studs

[F] 415.10.3 Floors in Storage Rooms

Floors in storage areas for corrosive liquids and highly toxic or toxic materials shall be of liquid-tight, noncombustible construction.

[F] 415.10.4 Separation of Highly Toxic Solids and Liquids

Highly toxic solids and liquids not stored in approved hazardous materials storage cabinets shall be isolated from other hazardous materials storage by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

[F] 415.11 Group H-5

In addition to the requirements set forth elsewhere in this code, Group H-5 shall comply with the provisions of Sections 415.11.1 through 415.11.12 and the California Fire Code.

[F] 415.11.1 Fabrication Areas

Fabrication areas shall comply with Sections 415.11.1.1 through 415.11.1.8.

[F] 415.11.1.1 Hazardous Materials

The aggregate quantities of hazardous materials stored and used in a single fabrication area shall not exceed the quantities set forth in Table 415.11.1.1.

Exception: The quantity limitations for any hazard category in Table 415.11.1.1 shall not apply where the fabrication area contains quantities of hazardous materials not exceeding the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2).

[F] TABLE 415.11.1.1— QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5a

| HAZARD CATEGORY |  | SOLIDS (pounds per square foot) | LIQUIDS (gallons per square foot) | GAS (cubic feet @ NTP/square foot) |
| --- | --- | --- | --- | --- |
| PHYSICAL-HAZARD MATERIALS |  |  |  |  |
| Combustible dust |  | Note b | Not Applicable | Not Applicable |
| Combustible fiber | Loose | Note b | Not Applicable | Not Applicable |
|  | Baled | Notes b and c |  |  |
| Combustible liquid | II | Not Applicable | 0.02 | Not Applicable |
|  | IIIA |  | 0.04 |  |
|  | IIIB |  | Not Limited |  |
| Combination Class | I, II and IIIA |  | 0.08 |  |
| Cryogenic gas | Flammable | Not Applicable | Not Applicable | Note d |
|  | Oxidizing |  |  | 2.5 |
| Explosives |  | Note b | Note b | Note b |
| Flammable gas | Gaseous | Not Applicable | Not Applicable | Note d |
|  | Liquefied |  |  | Note d |
| Flammable liquid | IA | Not Applicable | 0.005 | Not Applicable |
|  | IB |  | 0.05 |  |
|  | IC |  | 0.05 |  |
| Combination Class | IA, IB and IC |  | 0.05 |  |
| Combination Class | I, II and IIIA |  | 0.08 |  |
| Flammable solid |  | 0.002 | Not Applicable | Not Applicable |
| Organic peroxide | Unclassified detonable | Note b | Note b | Not Applicable |
|  | Class I | Note b | Note b |  |
|  | Class II | 0.05 | 0.0025 |  |
|  | Class III | 0.2 | 0.02 |  |
|  | Class IV | Not Limited | Not Limited |  |
|  | Class V | Not Limited | Not Limited |  |
| PHYSICAL-HAZARD MATERIALS |  |  |  |  |
| Oxidizing gas | Gaseous | Not Applicable | Not Applicable | 2.5 |
|  | Liquefied |  |  | 2.5 |
| Combination of gaseous and liquefied |  |  |  | 2.5 |
| Oxidizer | Class 4 | Note b | Note b | Not Applicable |
|  | Class 3 | 0.006 | 0.06 |  |
|  | Class 2 | 0.006 | 0.06 |  |
|  | Class 1 | 0.006 | 0.06 |  |
| Combination Class | 1, 2, 3 | 0.006 | 0.06 |  |
| Pyrophoric materials |  | Note b | 0.0025 | Notes d and e |
| Unstable (reactive) | Class 4 | Note b | Note b | Note b |
|  | Class 3 | 0.05 | 0.005 | Note b |
|  | Class 2 | 0.2 | 0.02 | Note b |
|  | Class 1 | Not Limited | Not Limited | Not Limited |
| Water reactive | Class 3 | 0.02f | 0.0025 | Not Applicable |
|  | Class 2 | 0.5 | 0.05 |  |
|  | Class 1 | Not Limited | Not Limited |  |
| HEALTH-HAZARD MATERIALS |  |  |  |  |
| Corrosives |  | Not Limited | Not Limited | Not Limited |
| Highly toxic |  | Not Limited | Not Limited | Note d |
| Toxics |  | Not Limited | Not Limited | Note d |

For SI: 1 pound = 0.454 kg, 1 pound per square foot = 4.882 kg/m2, 1 gallon per square foot = 40.7 L/m2, 1 cubic foot @ NTP/square foot = 0.305 m3 @ NTP/m2, 1 cubic foot = 0.02832 m3.

- Hazardous materials within piping shall not be included in the calculated quantities.

- Quantity of hazardous materials in a single fabrication shall not exceed the maximum allowable quantities per control area in Tables 307.1(1) and 307.1(2).

- Densely packed baled cotton that complies with the packing requirements of ISO 8115 shall not be included in this material class.

- The aggregate quantity of flammable, pyrophoric, toxic and highly toxic gases shall not exceed the greater of 0.2 cubic feet at NTP/square foot or 9,000 cubic feet at NTP.

- The aggregate quantity of pyrophoric gases in the building shall not exceed the amounts set forth in Table 415.6.5.

- Quantity of Class 3 water-reactive solids in a single tool shall not exceed 1 pound.

[F] 415.11.1.2 Separation

Assembly

Diagram

Fabrication areas, whose sizes are limited by the quantity of hazardous materials allowed by Table 415.11.1.1, shall be separated from each other, from corridors and from other parts of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

Exceptions:

- Doors within such fire barrier walls, including doors to corridors, shall be only self-closing fire door assemblies having a fire protection rating of not less than 3/4 hour.

- Windows between fabrication areas and corridors are permitted to be fixed glazing listed and labeled for a fire protection rating of not less than 3/4 hour in accordance with Section 716.

UpCodes Diagram (1)

Fire Protective vs. Fire Resistive Glazing

Assembly (1)

13-1.1: 1hr Steel Studs

Building products (4)

GPX® Ballistic

SaftiFirst

SuperClear® 45-HS

SaftiFirst

SuperClear® 45-HS-LI

SaftiFirst

SuperLite® X-45/60/90

SaftiFirst

[F] 415.11.1.3 Location of Occupied Levels

Diagram

Occupied levels of fabrication areas shall be located at or above the first story above grade plane.

UpCodes Diagram (1)

Grade Plane

[F] 415.11.1.4 Floors

Except for surfacing, floors within fabrication areas shall be of noncombustible construction.

Openings through floors of fabrication areas are permitted to be unprotected where the interconnected levels are used solely for mechanical equipment directly related to such fabrication areas (see Section 415.11.1.5).

Floors forming a part of an occupancy separation shall be liquid tight.

[F] 415.11.1.5 Shafts and Openings Through Floors

Elevator hoistways, vent shafts and other openings through floors shall be enclosed where required by Sections 712 and 713. Mechanical, duct and piping penetrations within a fabrication area shall not extend through more than two floors. The annular space around penetrations for cables, cable trays, tubing, piping, conduit or ducts shall be sealed at the floor level to restrict the movement of air. The fabrication area, including the areas through which the ductwork and piping extend, shall be considered to be a single conditioned environment.

[F] 415.11.1.6 Ventilation

Mechanical exhaust ventilation at the rate of not less than 1 cubic foot per minute per square foot [0.0051 m3/(s × m2)] of floor area shall be provided throughout the portions of the fabrication area where HPM are used or stored. The exhaust air duct system of one fabrication area shall not connect to another duct system outside that fabrication area within the building.

A ventilation system shall be provided to capture and exhaust gases, fumes and vapors at workstations.

Two or more operations at a workstation shall not be connected to the same exhaust system where either one or the combination of the substances removed could constitute a fire, explosion or hazardous chemical reaction within the exhaust duct system.

Exhaust ducts penetrating fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 shall be contained in a shaft of equivalent fire-resistance-rated construction. Exhaust ducts shall not penetrate fire walls.

Fire dampers shall not be installed in exhaust ducts.

[F] 415.11.1.7 Transporting Hazardous Production Materials to Fabrication Areas

HPM shall be transported to fabrication areas through enclosed piping or tubing systems that comply with Section 415.11.7, through service corridors complying with Section 415.11.3, or in corridors as permitted in the exception to Section 415.11.2. The handling or transporting of HPM within service corridors shall comply with the California Fire Code.

[F] 415.11.1.8 Electrical

Diagram

Electrical equipment and devices within the fabrication area shall comply with the California Electrical Code. The requirements for hazardous locations need not be applied where the average air change is not less than four times that set forth in Section 415.11.1.6 and where the number of air changes at any location is not less than three times that required by Section 415.11.1.6. The use of recirculated air shall be permitted.

UpCodes Diagrams (5)

Elect. Equip.: Entrance/Egress from Working Space, pt. 1

Elect. Equip.: Entrance/Egress from Working Space, pt. 3

Elect. Equip.: Entrance/Egress from Working Space, pt. 2

Allowed Clearance at Open Equipment Doors (<1000V)

Clearances at Electrical Equipment

[F] 415.11.1.8.1 Workstations

Workstations shall not be energized without adequate exhaust ventilation. See Section 415.11.1.6 for workstation exhaust ventilation requirements.

[F] 415.11.2 Corridors

Corridors shall comply with Chapter 10 and shall be separated from fabrication areas as specified in Section 415.11.1.2. Corridors shall not contain HPM and shall not be used for transporting such materials except through closed piping systems as provided in Section 415.11.7.4.

Exception: Where existing fabrication areas are altered or modified, HPM is allowed to be transported in existing corridors, subject to the following conditions:

- Nonproduction HPM is allowed to be transported in corridors if utilized for maintenance, lab work and testing.

- Where existing fabrication areas are altered or modified, HPM is allowed to be transported in existing corridors, subject to the following conditions:

  - Corridors. Corridors adjacent to the fabrication area where the alteration work is to be done shall comply with Section 1020 for a length determined as follows:

    - The length of the common wall of the corridor and the fabrication area; and

    - For the distance along the corridor to the point of entry of HPM into the corridor serving that fabrication area.

  - Emergency alarm system. There shall be an emergency telephone system, a local manual alarm station or other approved alarm-initiating device within corridors at not more than 150-foot (45 720 mm) intervals and at each exit and doorway. The signal shall be relayed to an approved central, proprietary or remote station service or the emergency control station and shall initiate a local audible alarm.

  - Pass-throughs. Self-closing doors having a fire protection rating of not less than 1 hour shall separate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors and protected by an approved automatic sprinkler system.

[F] 415.11.3 Service Corridors

Service corridors within a Group H-5 occupancy shall comply with Sections 415.11.3.1 through 415.11.3.4.

[F] 415.11.3.1 Use Conditions

Service corridors shall be separated from corridors as required by Section 415.11.1.2. Service corridors shall not be used as a required corridor.

[F] 415.11.3.2 Mechanical Ventilation

Service corridors shall be mechanically ventilated as required by Section 415.11.1.6 or at not less than six air changes per hour.

[F] 415.11.3.3 Means of Egress

The distance of travel from any point in a service corridor to an exit, exit access corridor or door into a fabrication area shall be not greater than 75 feet (22 860 mm). Dead ends shall be not greater than 4 feet (1219 mm) in length. There shall be not less than two exits, and not more than one-half of the required means of egress shall require travel into a fabrication area. Doors from service corridors shall swing in the direction of egress travel and shall be self-closing.

[F] 415.11.3.4 Minimum Width

The clear width of a service corridor shall be not less than 5 feet (1524 mm), or 33 inches (838 mm) wider than the widest cart or truck used in the service corridor, whichever is greater.

[F] 415.11.4 Emergency Alarm System

Emergency alarm systems shall be provided in accordance with this section and Sections 415.5.1 and 415.5.2. The maximum allowable quantity per control area provisions shall not apply to emergency alarm systems required for HPM.

[F] 415.11.4.1 Service Corridors

An emergency alarm system shall be provided in service corridors, with not fewer than one alarm device in each service corridor.

[F] 415.11.4.2 Corridors and Interior Exit Stairways and Ramps

Emergency alarms for corridors, interior exit stairways and ramps and exit passageways shall comply with Section 415.5.2.

[F] 415.11.4.3 Liquid Storage Rooms, HPM Rooms and Gas Rooms

Emergency alarms for liquid storage rooms, HPM rooms and gas rooms shall comply with Section 415.5.1.

[F] 415.11.4.4 Alarm-Initiating Devices

An approved emergency telephone system, local alarm manual pull stations, or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.

[F] 415.11.4.5 Alarm Signals

Activation of the emergency alarm system shall sound a local alarm and transmit a signal to the emergency control station.

[F] 415.11.5 Storage of Hazardous Production Materials

Storage of hazardous production materials (HPM) in fabrication areas shall be within approved or listed storage cabinets or gas cabinets or within a workstation. The storage of HPM in quantities greater than those specified in Section 5004.2 of the California Fire Code shall be in liquid storage rooms, HPM rooms or gas rooms as appropriate for the materials stored. The storage of other hazardous materials shall be in accordance with other applicable provisions of this code and the California Fire Code.

[F] 415.11.6 HPM Rooms, Gas Rooms, Liquid Storage Room Construction

HPM rooms, gas rooms and liquid shall be constructed in accordance with Sections 415.11.6.1 through 415.11.6.9.

[F] 415.11.6.1 HPM Rooms and Gas Rooms

Assembly

HPM rooms and gas rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours where the area is 300 square feet (27.9 m2) or more and not less than 1 hour where the area is less than 300 square feet (27.9 m2).

Assembly (1)

13-1.2: 2hr, Steel Studs

[F] 415.11.6.2 Liquid Storage Rooms

Assembly

Liquid storage rooms shall be constructed in accordance with the following requirements:

- Rooms greater than 500 square feet (46.5 m2) in area, shall have not fewer than one exterior door approved for fire department access.

- Rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 1 hour for rooms up to 150 square feet (13.9 m2) in area and not less than 2 hours where the room is more than 150 square feet (13.9 m2) in area.

- Shelving, racks and wainscotting in such areas shall be of noncombustible construction or wood of not less than 1-inch (25 mm) nominal thickness or fire-retardant-treated wood complying with Section 2303.2.

- Rooms used for the storage of Class I flammable liquids shall not be located in a basement.

Assemblies (22)

12-1.2: 2hr, Wood

6-1.2: 1hr & 2hr, Solid Gyp Plaster

6-2.2: 1hr & 2hr, Solid Gyp

27-1.1: 1hr, I-joist

30-1.1: 2hr, I-joist

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

6-1.1: 1hr & 2hr, Steel

6-5.1: 2hr Steel

6-4.1: 2hr Steel - Opt. 2 & 3

Show 12 more

Building product (1)

FF109X 2 Hour UL Fire Rated Recessed Light Cover

Tenmat

[F] 415.11.6.3 Floors

Except for surfacing, floors of HPM rooms and liquid storage rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials.

[F] 415.11.6.4 Location

Where HPM rooms, liquid storage rooms and gas rooms are provided, they shall have not fewer than one exterior wall and such wall shall be not less than 30 feet (9144 mm) from lot lines, including lot lines adjacent to public ways.

[F] 415.11.6.5 Explosion Control

Explosion control shall be provided where required by Section 414.5.1.

[F] 415.11.6.6 Exits

Where two exits are required from HPM rooms, liquid storage rooms and gas rooms, one shall be directly to the outside of the building.

[F] 415.11.6.7 Doors

Doors in a fire barrier wall, including doors to corridors, shall be self-closing fire door assemblies having a fire protection rating of not less than3/4 hour.

[F] 415.11.6.8 Ventilation

Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less than 1 cubic foot per minute per square foot (0.044 L/s/m2) of floor area or six air changes per hour.

Exhaust ventilation for gas rooms shall be designed to operate at a negative pressure in relation to the surrounding areas and direct the exhaust ventilation to an exhaust system.

[F] 415.11.6.9 Emergency Alarm System

An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms.

Emergency alarm-initiating devices shall be installed outside of each interior exit door of such rooms.

Activation of an emergency alarm-initiating device shall sound a local alarm and transmit a signal to the emergency control station.

An approved emergency telephone system, local alarm manual pull stations or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.

[F] 415.11.7 Piping and Tubing

Hazardous production materials piping and tubing shall comply with this section and ASME B31.3.

[F] 415.11.7.1 HPM Having a Health-Hazard Ranking of 3 or 4

Systems supplying HPM liquids or gases having a health-hazard ranking of 3 or 4 shall be welded throughout, except for connections, to the systems that are within a ventilated enclosure if the material is a gas, or an approved method of drainage or containment is provided for the connections if the material is a liquid.

[F] 415.11.7.2 Location in Service Corridors

Hazardous production materials supply piping or tubing in service corridors shall be exposed to view.

[F] 415.11.7.3 Excess Flow Control

Where HPM gases or liquids are carried in pressurized piping above 15 pounds per square inch gauge (psig) (103.4 kPa), excess flow control shall be provided. Where the piping originates from within a liquid storage room, HPM room or gas room, the excess flow control shall be located within the liquid storage room, HPM room or gas room. Where the piping originates from a bulk source, the excess flow control shall be located as close to the bulk source as practical.

[F] 415.11.7.4 Installations in Corridors and Above Other Occupancies

The installation of HPM piping and tubing within the space defined by the walls of corridors and the floor or roof above, or in concealed spaces above other occupancies, shall be in accordance with Sections 415.11.7.1 through 415.11.7.3 and the following conditions:

- Automatic sprinklers shall be installed within the space unless the space is less than 6 inches (152 mm) in the least dimension.

- Ventilation not less than six air changes per hour shall be provided. The space shall not be used to convey air from any other area.

- Where the piping or tubing is used to transport HPM liquids, a receptor shall be installed below such piping or tubing. The receptor shall be designed to collect any discharge or leakage and drain it to an approved location. The 1-hour enclosure shall not be used as part of the receptor.

- HPM supply piping and tubing and nonmetallic waste lines shall be separated from the corridor and from occupancies other than Group H-5 by fire barriers or by an approved method or assembly that has a fire-resistance rating of not less than 1 hour. Access openings into the enclosure shall be protected by approved fire-protection-rated assemblies.

- Ready access to manual or automatic remotely activated fail-safe emergency shutoff valves shall be installed on piping and tubing other than waste lines at the following locations:

  - At branch connections into the fabrication area.

  - At entries into corridors.

Exception: Transverse crossings of the corridors by supply piping that is enclosed within a ferrous pipe or tube for the width of the corridor need not comply with Items 1 through 5.

[F] 415.11.7.5 Identification

Piping, tubing and HPM waste lines shall be identified in accordance with ANSI A13.1 to indicate the material being transported.

[F] 415.11.8 Gas Detection Systems

A gas detection system complying with Section 916 shall be provided for HPM gases where the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases in accordance with Sections 415.11.8.1 through 415.11.8.2.

[F] 415.11.8.1 Where Required

A gas detection system shall be provided in the areas identified in Sections 415.11.8.1.1 through 415.11.8.1.4.

[F] 415.11.8.1.1 Fabrication Areas

A gas detection system shall be provided in fabrication areas where HPM gas is used in the fabrication area.

[F] 415.11.8.1.2 HPM Rooms

A continuous gas detection system shall be provided in HPM rooms where HPM gas is used in the room.

[F] 415.11.8.1.3 Gas Cabinets, Exhausted Enclosures and Gas Rooms

A gas detection system shall be provided in gas cabinets and exhausted enclosures for HPM gas. A gas detection system shall be provided in gas rooms where HPM gases are not located in gas cabinets or exhausted enclosures.

[F] 415.11.8.1.4 Corridors

Where HPM gases are transported in piping placed within the space defined by the walls of a corridor and the floor or roof above the corridor, a gas detection system shall be provided where piping is located and in the corridor.

Exception: A gas detection system is not required for occasional transverse crossings of the corridors by supply piping that is enclosed in a ferrous pipe or tube for the width of the corridor.

[F] 415.11.8.2 Gas Detection System Operation

The gas detection system shall be capable of monitoring the room, area or equipment in which the HPM gas is located at or below all the following gas concentrations:

- Immediately dangerous to life and health (IDLH) values where the monitoring point is within an exhausted enclosure, ventilated enclosure or gas cabinet.

- Permissible exposure limit (PEL) levels where the monitoring point is in an area outside an exhausted enclosure, ventilated enclosure or gas cabinet.

- For flammable gases, the monitoring detection threshold level shall be vapor concentrations in excess of 25 percent of the lower flammable limit (LFL) where the monitoring is within or outside an exhausted enclosure, ventilated enclosure or gas cabinet.

- Except as noted in this section, monitoring for highly toxic and toxic gases shall also comply with Chapter 60 of the California Fire Code.

[F] 415.11.8.2.1 Alarms

The gas detection system shall initiate a local alarm and transmit a signal to the emergency control station when a short-term hazard condition is detected. The alarm shall be both visual and audible and shall provide warning both inside and outside the area where the gas is detected. The audible alarm shall be distinct from all other alarms.

[F] 415.11.8.2.2 Shutoff of Gas Supply

The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for which gas is detected when a short-term hazard condition is detected. Automatic closure of shutoff valves shall comply with the following:

- Where the gas detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close.

- Where the gas detection sampling point initiating the gas detection system alarm is within a room and compressed gas containers are not in gas cabinets or an exhausted enclosure, the shutoff valves on all gas lines for the specific gas detected shall automatically close.

- Where the gas detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve supplying the manifold for the compressed gas container of the specific gas detected shall automatically close.

Exception: Where the gas detection sampling point initiating the gas detection system alarm is at the use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve for the branch line located in the piping distribution manifold enclosure shall automatically close.

[F] 415.11.9 Manual Fire Alarm System

An approved manual fire alarm system shall be provided throughout buildings containing Group H-5. Activation of the alarm system shall initiate a local alarm and transmit a signal to the emergency control station. The fire alarm system shall be designed and installed in accordance with Section 907.

[F] 415.11.10 Emergency Control Station

An emergency control station shall be provided in accordance with Sections 415.11.10.1 through 415.11.10.3.

[F] 415.11.10.1 Location

The emergency control station shall be located on the premises at an approved location outside the fabrication area.

[F] 415.11.10.2 Staffing

Trained personnel shall continuously staff the emergency control station.

[F] 415.11.10.3 Signals

The emergency control station shall receive signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detection systems shall include, but not be limited to, the following where such equipment or systems are required to be provided either in this chapter or elsewhere in this code:

- Automatic sprinkler system alarm and monitoring systems.

- Manual fire alarm systems.

- Emergency alarm systems.

- Gas detection systems.

- Smoke detection systems.

- Emergency power system.

- Automatic detection and alarm systems for pyrophoric liquids and Class 3 water-reactive liquids required in Section 2705.2.3.4 of the California Fire Code.

- Exhaust ventilation flow alarm devices for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in Section 2705.2.3.4 of the California Fire Code.

[F] 415.11.11 Emergency Power System

An emergency power system shall be provided in Group H-5 occupancies in accordance with Section 2702. The emergency power system shall supply power automatically to the electrical systems specified in Section 415.11.11.1 when the normal electrical supply system is interrupted.

[F] 415.11.11.1 Required Electrical Systems

Emergency power shall be provided for electrically operated equipment and connected control circuits for the following systems:

- HPM exhaust ventilation systems.

- HPM gas cabinet ventilation systems.

- HPM exhausted enclosure ventilation systems.

- HPM gas room ventilation systems.

- HPM gas detection systems.

- Emergency alarm systems.

- Manual and automatic fire alarm systems.

- Automatic sprinkler system monitoring and alarm systems.

- Automatic alarm and detection systems for pyrophoric liquids and Class 3 water-reactive liquids required in Section 2705.2.3.4 of the California Fire Code.

- Flow alarm switches for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in Section 2705.2.3.4 of the California Fire Code.

- Electrically operated systems required elsewhere in this code or in the California Fire Code applicable to the use, storage or handling of HPM.

[F] 415.11.11.2 Exhaust Ventilation Systems

Exhaust ventilation systems are allowed to be designed to operate at not less than one-half the normal fan speed on the emergency power system where it is demonstrated that the level of exhaust will maintain a safe atmosphere.

[F] 415.11.12 Automatic Sprinkler System Protection in Exhaust Ducts for HPM

An approved automatic sprinkler system shall be provided in exhaust ducts conveying gases, vapors, fumes, mists or dusts generated from HPM in accordance with Sections 415.11.12.1 through 415.11.12.3 and the California Mechanical Code.

[F] 415.11.12.1 Metallic and Noncombustible Nonmetallic Exhaust Ducts

An approved automatic sprinkler system shall be provided in metallic and noncombustible nonmetallic exhaust ducts where all of the following conditions apply:

- Where the largest cross-sectional diameter is equal to or greater than 10 inches (254 mm).

- The ducts are within the building.

- The ducts are conveying flammable gases, vapors or fumes.

[F] 415.11.12.2 Combustible Nonmetallic Exhaust Ducts

Automatic sprinkler system protection shall be provided in combustible nonmetallic exhaust ducts where the largest cross-sectional diameter of the duct is equal to or greater than 10 inches (254 mm).

Exception: Ducts need not be provided with automatic sprinkler protection as follows:

- Ducts listed or approved for applications without automatic sprinkler system protection.

- Ducts not more than 12 feet (3658 mm) in length installed below ceiling level.

[F] 415.11.12.3 Automatic Sprinkler Locations

Automatic sprinklers shall be installed at 12-foot (3658 mm) intervals in horizontal ducts and at changes in direction. In vertical ducts, sprinklers shall be installed at the top and at alternate floor levels.

415.12 Group H Occupancies Located on the 11th Story and Above

415.12.1 Fire — Smoke Barrier

Any story containing a Group H occupancy on the 11th story and above shall be subdivided by a fire-smoke barrier constructed as a fire barrier having a fire resistance rating of not less than 2 hours and shall also comply with the smoke barrier requirements of Section 710. The 2-hour fire-smoke barrier shall be in accordance with Sections 415.12.1.1 through 415.12.1.5.

415.12.1.1

The 2-hour fire-smoke barrier shall be continuous from exterior wall to exterior wall.

415.12.1.2

The fire-smoke barrier shall divide the story so that the square footage on each side of the 2-hour fire-smoke barrier is not less than 30 percent of the total floor area.

415.12.1.3

A minimum of one door opening shall be provided in the 2-hour fire-smoke barrier for emergency access.

415.12.1.4

Each side of the 2-hour fire-smoke barrier shall be designed as a separate smoke zone designed in accordance with Section 909.5.

415.12.1.5

The area on each side of the 2-hour fire-smoke barrier shall be served by a minimum of one exit enclosure in accordance with Section 1022.

415.13 Elevators and Elevator Lobbies on the 11th Story and Above

Any story containing a Group H occupancy on the 11th story and above shall be provided with elevators and elevator lobbies in accordance with Sections 415.13.1 through 415.13.3.

415.13.1

An elevator that serves every story of the building shall be provided on each side of the 2-hour fire-smoke barrier.

415.13.2

An elevator lobby shall be provided on each side of the 2-hour fire-smoke barrier at each floor in accordance with Section 708.4. Exceptions to 708.4 shall not apply.

415.13.3

The elevator and its associated elevator lobbies and elevator machine rooms shall be pressurized in accordance with Section 909.5.

Section 416 Spray Application of Flammable Finishes

[F] 416.1 General

The provisions of this section shall apply to the construction, installation and use of buildings and structures, or parts thereof, for the spray application of flammable finishes. Operations and equipment shall comply with the California Fire Code .

[F] 416.2 Spray Rooms

Assembly

Spray rooms shall be enclosed with not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Floors shall be waterproofed and drained in an approved manner.

Assembly (1)

13-1.1: 1hr Steel Studs

[F] 416.2.1 Construction

Walls and ceilings of spray rooms shall be constructed of noncombustible materials or the interior surface shall be completely covered with noncombustible materials. Aluminum shall not be used.

[F] 416.2.2 Surfaces

The interior surfaces of spray rooms shall be smooth and shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning, and shall be so designed to confine residues within the room.

[F] 416.2.3 Ventilation

Mechanical ventilation and interlocks with the spraying operation shall be in accordance with the California Fire Code and California Mechanical Code.

[F] 416.3 Spraying Spaces

Spraying spaces shall be ventilated with an exhaust system to prevent the accumulation of flammable mist or vapors in accordance with the California Mechanical Code. Where such spaces are not separately enclosed, noncombustible spray curtains shall be provided to restrict the spread of flammable vapors.

[F] 416.3.1 Surfaces

The interior surfaces of spraying spaces shall be smooth; shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning; and shall be so designed to confine residues within the spraying space. Aluminum shall not be used.

[F] 416.4 Spray Booths

Spray booths shall be designed, constructed and operated in accordance with the California Fire Code.

[F] 416.5 Fire Protection

An automatic sprinkler system or fire-extinguishing system shall be provided in all spray rooms and spray booths, and shall be installed in accordance with Chapter 9.

Section 417 Drying Rooms

[F] 417.1 General

A drying room or dry kiln installed within a building shall be constructed entirely of approved noncombustible materials or assemblies of such materials regulated by the approved rules or as required in the general and specific sections of this chapter for special occupancies and where applicable to the general requirements of the California Mechanical Code.

[F] 417.2 Piping Clearance

Overhead heating pipes shall have a clearance of not less than 2 inches (51 mm) from combustible contents in the dryer.

[F] 417.3 Insulation

Where the operating temperature of the dryer is 175°F (79°C) or more, metal enclosures shall be insulated from adjacent combustible materials by not less than 12 inches (305 mm) of airspace, or the metal walls shall be lined with 1/4-inch (6.4 mm) insulating mill board or other approved equivalent insulation.

[F] 417.4 Fire Protection

Drying rooms designed for high-hazard materials and processes, including special occupancies as provided for in Chapter 4, shall be protected by an approved automatic fire-extinguishing system complying with the provisions of Chapter 9.

Section 418 Organic Coatings

[F] 418.1 Building Features

Manufacturing of organic coatings shall be done only in buildings that do not have pits or basements.

[F] 418.2 Location

Organic coating manufacturing operations and operations incidental to or connected therewith shall not be located in buildings having other occupancies.

[F] 418.3 Process Mills

Mills operating with close clearances and that process flammable and heat-sensitive materials, such as nitrocellulose, shall be located in a detached building or noncombustible structure.

[F] 418.4 Tank Storage

Storage areas for flammable and combustible liquid tanks inside of structures shall be located at or above grade and shall be separated from the processing area by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

[F] 418.5 Nitrocellulose Storage

Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

[F] 418.6 Finished Products

Assembly

Storage rooms for finished products that are flammable or combustible liquids shall be separated from the processing area by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.

Assembly (1)

13-1.2: 2hr, Steel Studs

Section 419 Artificial Decorative Vegetation

[F] 419.1 Artificial Decorative Vegetation

Artificial decorative vegetation exceeding 6 feet (1830 mm) in height and permanently installed outdoors within 5 feet (1524 mm) of a building, or on the roof of a building, shall comply with Section 321.1 of the California Fire Code.

Exception: Artificial decorative vegetation located more than 30 feet (9144 mm) from the exterior wall of a building.

Section 420 Groups R-1, R-2, R-2.1, R-2.2, R-3, R-3.1 and R-4

420.1 General

Occupancies in Groups R-1, R-2, R-2.1, R-2.2, R-3, R-3.1 and R-4 shall comply with the provisions of Sections 420.1 through 420.11 and other applicable provisions of this code.

420.2 Separation Walls

Walls separating dwelling units in the same building, walls separating sleeping units in the same building, walls separating dwelling units from sleeping units in the same building and walls separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as fire partitions in accordance with Section 708.

420.3 Horizontal Separation

Floor assemblies separating dwelling units in the same buildings, floor assemblies separating sleeping units in the same building, floor assemblies separating dwelling units from sleeping units in the same building and floor assemblies separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as horizontal assemblies in accordance with Section 711.

[F] 420.4 Automatic Sprinkler System

Group R occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.8. Group R-2.2 shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. Group R-2.1 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6. Quick-response or residential automatic sprinklers shall be installed in accordance with Section 903.3.2.

[F] 420.5 Fire Alarm Systems and Smoke Alarms

Fire alarm systems and smoke alarms shall be provided in Group R-1, R-2 and R-2.1 occupancies in accordance with Sections 907.2.6, 907.2.8 and 907.2.9 and 907.2.10, respectively. Single- or multiple-station smoke alarms shall be provided in Groups R-2, R-2.1, R-3 and R-4 in accordance with Section 907.2.11. Group R-2.2 shall be equipped throughout with an automatic fire alarm systems per 907.2.9.2 and shall have a manual fire alarm pull station at the 24-hour staff watch office.

420.6 Smoke Barriers in Group R-2.1

Smoke barriers shall be provided in Group R-2.1 to subdivide every story used by persons receiving care, treatment or sleeping and to provide other stories with an occupant load of 50 or more persons, into not fewer than two smoke compartments. Such stories shall be divided into smoke compartments with an area of not more than 22,500 square feet (2092 m2) and the distance of travel from any point in a smoke compartment to a smoke barrier door shall not exceed 200 feet (60 960 mm). The smoke barrier shall be in accordance with Section 709.

420.6.1 Smoke Barrier in Group R-2.2

Occupancies in Group R-2.2 shall have smoke barriers complying with Sections 709 to divide every story occupied by residents for sleeping, into no fewer than two smoke compartments.

Exception: Spaces having a direct exit to a public way.

420.6.2 Refuge Area

Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:

- Not less than 15 net square feet (1.4 m2) for each care recipient.

- Not less than 6 net square feet (0.56 m2) for other occupants.

Areas or spaces permitted to be included in the calculation of the refuge area are corridors, lounge or dining areas and other low-hazard areas.

420.7

Reserved.

420.8

Reserved.

420.9 Domestic Cooking Appliances

In Group R-2.1 occupancies, installation of cooking appliance used in domestic cooking facilities shall comply with all of the following:

- The types of cooking appliances permitted shall be limited to ovens, cooktops, ranges, warmers and microwaves.

- Domestic cooking hoods installed and constructed in accordance with the California Mechanical Code shall be provided over cooktops or ranges.

- Cooktops and ranges shall be protected in accordance with Section 904.15.

- A shutoff for the fuel and electrical supply to the cooking equipment shall be provided in a location to which only staff has access.

- A timer shall be provided that automatically deactivates the cooking appliances within a period of not more than 120 minutes.

- A portable fire extinguisher shall be provided. Installation shall be in accordance with Section 906 and the extinguisher shall be located within a 30-foot (9144 mm) distance of travel from each domestic cooking appliance.

Exceptions:

- Cooking facilities provided within care recipients' individual dwelling units are not required to comply with this section.

- Cooktops and ranges used for care-recipient training or nutritional counseling are not required to comply with Item 3 of this section.

420.10 Group R Cooking Facilities

In Group R occupancies, cooking appliances used for domestic cooking operations shall be in accordance with the California Mechanical Code.

420.11 Group R-2 Dormitory Cooking Facilities

Domestic cooking appliances for use by residents of Group R-2 college dormitories shall be in accordance with Sections 420.11.1 and 420.11.2.

420.11.1 Cooking Appliances

Where located in Group R-2 college dormitories, domestic cooking appliances for use by residents shall be in compliance with all of the following:

- The types of domestic cooking appliances shall be limited to ovens, cooktops, ranges, warmers, coffee makers and microwaves.

- Domestic cooking appliances shall be limited to approved locations.

- Cooktops and ranges shall be protected in accordance with Section 904.15.

- Cooktops and ranges shall be provided with a domestic cooking hood installed and constructed in accordance with the California Mechanical Code. Kitchen range hoods shall also be rated for sound and meet field verification requirements in the California Energy Code for low-rise and high-rise residential buildings.

420.11.2 Cooking Appliances in Sleeping Rooms

Cooktops, ranges and ovens shall not be installed or used in sleeping rooms.

420.12 [HCD 1] Construction Waste Management

Recycle and/or salvage for reuse a minimum of 65 percent of the nonhazardous construction and demolition waste in accordance with the California Green Building Standards Code (CALGreen), Chapter 4, Division 4.4.

420.13 Special Provisions for Residential Hotels

[HCD 1 & HCD 1-AC]

420.13.1 Locking Mail Receptacles

A locking mail receptacle for each residential unit shall be provided in all residential hotels pursuant to the requirements specified in Health and Safety Code Section 17958.3.

420.14 [HCD 1] Electric Vehicle (EV) Charging for New Construction

Newly constructed Group R-1, R-2 and R-3 buildings shall meet requirements for electric vehicle charging in accordance with the California Green Building Standards Code (CALGreen), Chapter 4, Division 4.1.

420.15 Licensed 24-Hour Care Facilities in a Group R-2.1, R-3.1 or R-4 Occupancy

See Section 435 for Special Provisions for licensed 24-hour care facilities in a Group R-2.1, R-3.1 or R-4 occupancy.

420.16 Electronic Monitoring

In Group R-2.2 occupancies there shall be continuous electronic supervision via CCTV system camera coverage and monitoring the following areas: corridors, storage rooms over 100 square feet, central kitchen and main entryway of the facility.

Section 421 Hydrogen Fuel Gas Rooms

[F] 421.1 General

Where required by the California Fire Code, hydrogen fuel gas rooms shall be designed and constructed in accordance with Sections 421.1 through 421.7.

[F] 421.2 Location

Hydrogen fuel gas rooms shall not be located below grade.

[F] 421.3 Design and Construction

Hydrogen fuel gas rooms not classified as Group H shall be separated from other areas of the building in accordance with Section 509.1.

[F] 421.3.1 Pressure Control

Hydrogen fuel gas rooms shall be provided with a ventilation system designed to maintain the room at a negative pressure in relation to surrounding rooms and spaces.

[F] 421.3.2 Windows

Operable windows in interior walls shall not be permitted. Fixed windows shall be permitted where in accordance with Section 716.

[F] 421.4 Exhaust Ventilation

Hydrogen fuel gas rooms shall be provided with mechanical exhaust ventilation in accordance with the applicable provisions of the California Mechanical Code.

[F] 421.5 Gas Detection System

Hydrogen fuel gas rooms shall be provided with a gas detection system that complies with Sections 421.5.1, 421.5.2, and 916.

[F] 421.5.1 System Activation

Activation of a gas detection alarm shall result in both of the following:

- Initiation of distinct audible and visible alarm signals both inside and outside of the hydrogen fuel gas room.

- Automatic activation of the mechanical exhaust ventilation system.

[F] 421.5.2 Failure of the Gas Detection System

Failure of the gas detection system shall automatically activate the mechanical exhaust ventilation system, stop hydrogen generation, and cause a trouble signal to sound at an approved location.

[F] 421.6 Explosion Control

Explosion control shall be provided where required by Section 414.5.1.

[F] 421.7 Standby Power

Diagram

Mechanical ventilation and gas detection systems shall be provided with a standby power system in accordance with Section 2702.

UpCodes Diagram (1)

Standby Power Systems

Section 422 Ambulatory Care Facilities

422.1 General

Occupancies classified as ambulatory care facilities shall comply with the provisions of Sections 422.1 through 422.7 and other applicable provisions of this code. [For OSHPD 3] For clinics licensed by California Department of Public Health also refer to Section 1226.2.

422.2 Separation

Ambulatory care facilities where the potential for four or more care recipients are to be incapable of self-preservation at any time shall be separated from adjacent spaces, corridors or tenants with a 1-hour fire barrier installed in accordance with Section 707.

422.3 Smoke Compartments

Where the aggregate area of one or more ambulatory care facilities is greater than 10,000 square feet (929 m2) on one story, the story shall be provided with a smoke barrier to subdivide the story into not fewer than two smoke compartments. The area of any one such smoke compartment shall be not greater than 22,500 square feet (2092 m2). The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm). The smoke barrier shall be installed in accordance with Section 709 with the exception that smoke barriers shall be continuous from outside wall to an outside wall, a floor to a floor, or from a smoke barrier to a smoke barrier or a combination thereof.

Building products (3)

SuperLite® II-XL 60

SaftiFirst

SuperLite® II-XLB 60

SaftiFirst

SuperLite® II-XLM 60

SaftiFirst

422.3.1 Means of Egress

Where ambulatory care facilities require smoke compartmentation in accordance with Section 422.3, the fire safety evacuation plans provided in accordance with Section 1002.2 shall identify the building components necessary to support a defend-in-place emergency response in accordance with Sections 403 and 404 of the California Fire Code.

422.3.2 Refuge Area

Not less than 30 net square feet (2.8 m2) for each nonambulatory care recipient and not less than 15 net square feet (1.4 m2) per ambulatory occupant shall be provided within the aggregate area of corridors, care recipient rooms, treatment rooms, lounge or dining areas and other low-hazard areas within each smoke compartment. Each occupant of an ambulatory care facility shall be provided with access to a refuge area without passing through or utilizing adjacent tenant spaces.

422.3.3 Independent Egress

A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated.

422.3.4 Distance of Travel

The distance of travel between any point in an ambulatory care facility and an exit shall be not greater than 200 feet (60 960 mm).

[F] 422.4 Automatic Sprinkler Systems

Automatic sprinkler systems shall be provided for ambulatory care facilities in accordance with Section 903.2.2.

[F] 422.5 Fire Alarm Systems

A fire alarm system shall be provided for ambulatory care facilities in accordance with Section 907.2.2.

[F] 422.6 Electrical Systems

In ambulatory care facilities, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of Chapter 27 and California Electrical Code Article 517.

422.7 Domestic Cooking

In fully sprinklered buildings, the installation of cooking appliances used in domestic cooking facilities shall comply with all of the following:

- The types of cooking appliances permitted are limited to ovens, cooktops, ranges, warmers and microwaves.

- Domestic cooking hoods installed and constructed in accordance with Section 504.3 of the California Mechanical Code shall be provided over cooktops or ranges.

- A shutoff for the fuel and electrical supply to the cooking equipment shall be provided in a location to which only staff has access.

- A timer shall be provided that automatically deactivates the cooking appliances within a period of not more than 120 minutes.

- A portable fire extinguisher shall be provided. Installation shall be in accordance with Section 906 and the extinguisher shall be located within a 30-foot (9144 mm) distance of travel from each domestic cooking appliance.

- The area containing the domestic cooking appliances shall be separated from all other areas by fire partitions constructed complying with Section 708.

Section 423 Storm Shelters

423.1 General

This section applies to the design and construction of storm shelters constructed as separate detached buildings or constructed as rooms or spaces within buildings for the purpose of providing protection from tornadoes hurricanes and other severe windstorms during the storm. This section specifies where storm shelters are required and provides requirements for the design and construction of storm shelters. Design of facilities for use as emergency shelters after the storm are outside the scope of ICC 500 and shall comply with Table 1604.5 as a Risk Category IV Structure.

423.2 Construction

Storm shelters shall be constructed in accordance with this code and ICC 500 and shall be designated as hurricane shelters, tornado shelters, or combined hurricane and tornado shelters. Buildings or structures that are also designated as emergency shelters shall also comply with Table 1604.5 as Risk Category IV structures.

Any storm shelter not required by this section shall be permitted to be constructed, provided that such structures meet the requirements of this code and ICC 500.

423.3 Occupancy Classification

The occupancy classification for a storm shelter shall be determined in accordance with this section.

423.3.1 Dedicated Storm Shelters

A facility designed to be occupied solely as a storm shelter shall be classified as Group A-3 for the determination of requirements other than those covered in ICC 500.

Exceptions:

- The occupancy category for dedicated storm shelters with a design occupant capacity of less than 50 persons as determined in accordance with ICC 500 shall be in accordance with Section 303.

- The occupancy category for a dedicated residential storm shelter shall be the Group R occupancy served.

423.3.2 Storm Shelters Within Host Buildings

Where designated storm shelters are constructed as a room or space within a host building that will normally be occupied for other purposes, the requirements of this code for the occupancy of the building, or the individual rooms or spaces thereof, shall apply unless otherwise required by ICC 500.

423.4 Critical Emergency Operations

In areas where the shelter design wind speed for tornados in accordance with Figure 304.2(1) of ICC 500 is 250 mph, 911 call stations, emergency operation centers and fire, rescue, ambulance and police stations shall comply with Table 1604.5 as a Risk Category IV structure and shall be provided with a storm shelter constructed in accordance with ICC 500.

423.4.1 Design Occupant Capacity

The required design occupant capacity of the storm shelter shall include the critical emergency operations on the site and shall be the total occupant load of offices and the number of beds.

Exceptions:

- Where approved by the building official, the actual number of occupants for whom each occupied space, floor or building is designed, although less than that determined by occupant load calculation, shall be permitted to be used in the determination of the required design occupant capacity for the storm shelter.

- Where a new building is being added on an existing site, and where the new building is not of sufficient size to accommodate the required design occupant capacity of the storm shelter for all of the buildings on the site, the storm shelter shall accommodate not less than the required occupant capacity of the new building.

- Where approved by the building official, the required design occupant capacity of the shelter shall be permitted to be reduced by the design occupant capacity of any existing storm shelters on the site.

423.4.2 Location

Storm shelters shall be located within the building they serve or shall be located where the distance of travel from not fewer than one exterior door of each building to a door of the shelter serving that building does not exceed 1,000 feet (305 m), unless otherwise approved.

423.5 Group E Occupancies

In areas where the shelter design wind speed for tornados is 250 mph in accordance with Figure 304.2(1) of ICC 500, all Group E occupancies with an occupant load of 50 or more shall have a storm shelter constructed in accordance with ICC 500.

Exceptions:

- Group E day care facilities.

- Group E occupancies accessory to places of religious worship.

- Buildings meeting the requirements for shelter design in ICC 500.

423.5.1 Design Occupant Capacity

The required design occupant capacity of the storm shelter shall include all of the buildings on the site and shall be the total occupant load of the classrooms, vocational rooms and offices in the Group E occupancy.

Exceptions:

- Where approved by the building official, the actual number of occupants for whom each occupied space, floor or building is designed, although less than that determined by occupant load calculation, shall be permitted to be used in the determination of the required design occupant capacity for the storm shelter.

- Where a new building is being added on an existing Group E site, and where the new building is not of sufficient size to accommodate the required design occupant capacity of the storm shelter for all of the buildings on the site, the storm shelter shall accommodate not less than the required occupant capacity for the new building.

- Where approved by the building official, the required design occupant capacity of the shelter shall be permitted to be reduced by the design occupant capacity of any existing storm shelters on the site.

423.5.2 Location

Storm shelters shall be located within the buildings they serve or shall be located where the distance of travel from not fewer than one exterior door of each building to a door of the shelter serving that building does not exceed 1,000 feet (305 m).

Section 424 Play Structures

[BF] 424.1 General

Play structures installed inside all occupancies covered by this code that exceed 10 feet (3048 mm) in height or 150 square feet (14 m2) in area shall comply with Sections 424.2 through 424.5.

[BF] 424.2 Materials

Play structures shall be constructed of noncombustible materials or of combustible materials that comply with the following:

- Fire-retardant-treated wood complying with Section 2303.2.

- Light-transmitting plastics complying with Section 2606.

- Foam plastics (including the pipe foam used in soft-contained play equipment structures) having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289, using the 20 kW ignition source.

- Aluminum composite material (ACM) meeting the requirements of Class A interior finish in accordance with Chapter 8 when tested as an assembly in the maximum thickness intended for use.

- Textiles and films complying with the fire propagation performance criteria contained in Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

- Plastic materials used to construct rigid components of soft-contained play equipment structures (such as tubes, windows, panels, junction boxes, pipes, slides and decks) exhibiting a peak rate of heat release not exceeding 400 kW/ m2 when tested in accordance with ASTM E1354 at an incident heat flux of 50 kW/m2 in the horizontal orientation at a thickness of 6 mm.

- Ball pool balls, used in soft-contained play equipment structures, having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289, using the 20 kW ignition source. The minimum specimen test size shall be 36 inches by 36 inches (914 mm by 914 mm) by an average of 21 inches (533 mm) deep, and the balls shall be held in a box constructed of galvanized steel poultry netting wire mesh.

- Foam plastics shall be covered by a fabric, coating or film meeting the fire propagation performance criteria contained in Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

- The floor covering placed under the play structure shall exhibit a Class I interior floor finish classification, as described in Section 804, when tested in accordance with ASTM E648 or NFPA 253.

- Interior finishes for structures exceeding 600 square feet (56 m2) in area or 10 feet (3048 mm) in height shall have a flame spread index not greater than that specified in Table 803.13 for the occupancy group and location designated. Interior wall and ceiling finish materials tested in accordance with NFPA 286 and meeting the acceptance criteria of Section 803.1.1.1, shall be permitted to be used where a Class A classification in accordance with ASTM E84 or UL 723 is required.

[F] 424.3 Fire Protection

Play structures shall be provided with the same level of approved fire suppression and detection devices required for other structures in the same occupancy.

[BF] 424.4 Separation

Play structures shall have a horizontal separation from building walls, partitions and from elements of the means of egress of not less than 5 feet (1524 mm). Play structures shall have a horizontal separation from other play structures of not less than 20 feet (6090 mm).

[BF] 424.5 Area Limits

Play structures shall be not greater than 600 square feet (56 m2) in area, unless a special investigation, acceptable to the building official, has demonstrated adequate fire safety.

[BF] 424.5.1 Design

Play structures exceeding 600 square feet (56 m2) in area or 10 feet (3048 mm) in height shall be designed in accordance with Chapter 16.

Section 425 Hyperbaric Facilities

425.1 Hyperbaric Facilities

Hyperbaric facilities shall meet the requirements contained in Chapter 14 of NFPA 99.

[F] Section 426 Combustible Dusts, Grain Processing and Storage

[F] 426.1 General

The provisions of Sections 426.1.1 through 426.1.7 shall apply to buildings in which materials that produce combustible dusts are stored or handled. Buildings that store or handle combustible dusts shall comply with the applicable provisions of the California Fire Code. Where required by the fire code official, NFPA 652 and the applicable provisions of NFPA 61, NFPA 85, NFPA 120, NFPA 484, NFPA 654, NFPA 655 and NFPA 664 shall apply.

[F] 426.1.1 Type of Construction and Height Exceptions

Buildings shall be constructed in compliance with the height, number of stories and area limitations specified in Sections 504 and 506; except that where erected of Type I or II construction, the heights and areas of grain elevators and similar structures shall be unlimited, and where of Type IV construction, the maximum building height shall be 65 feet (19 812 mm) and except further that, in isolated areas, the maximum building height of Type IV structures shall be increased to 85 feet (25 908 mm).

[F] 426.1.2 Grinding Rooms

Assembly

Every room or space occupied for grinding or other operations that produce combustible dusts in such a manner that the room or space is classified as a Group H-2 occupancy shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating of the enclosure shall be not less than 2 hours where the area is not more than 3,000 square feet (279 m2), and not less than 4 hours where the area is greater than 3,000 square feet (279 m2).

Assemblies (27)

12-1.2: 2hr, Wood

6-1.2: 1hr & 2hr, Solid Gyp Plaster

6-2.2: 1hr & 2hr, Solid Gyp

27-1.1: 1hr, I-joist

30-1.1: 2hr, I-joist

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

6-1.1: 1hr & 2hr, Steel

6-5.1: 2hr Steel

6-4.1: 2hr Steel - Opt. 2 & 3

Show 17 more

Building product (1)

FF109X 2 Hour UL Fire Rated Recessed Light Cover

Tenmat

[F] 426.1.3 Conveyors

Conveyors, chutes, piping and similar equipment passing through the enclosures of rooms or spaces shall be constructed dirt tight and vapor tight, and be of approved noncombustible materials complying with Chapter 30.

[F] 426.1.4 Explosion Control

Explosion control shall be provided as specified in the California Fire Code, or spaces shall be equipped with the equivalent mechanical ventilation complying with the California Mechanical Code.

[F] 426.1.5 Grain Elevators

Grain elevators, malt houses and buildings for similar occupancies shall not be located 30 feet (9144 mm) or less from interior lot lines or structures on the same lot, except where erected along a railroad right-of-way.

[F] 426.1.6 Coal Pockets

Coal pockets located less than 30 feet (9144 mm) from interior lot lines or from structures on the same lot shall be constructed of not less than Type IB construction. Where more than 30 feet (9144 mm) from interior lot lines, or where erected along a railroad right-of-way, the minimum type of construction of such structures not more than 65 feet (19 812 mm) in building height shall be Type IV.

[F] 426.1.7 Tire Rebuilding

Buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operation by a 1-hour fire barrier.

Exception: Buffing operations are not required to be separated where all of the following conditions are met:

- Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action.

- Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/s) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity.

- The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow.

Section 427 Medical Gas Systems

[F] 427.1 General

Medical gases at health care-related facilities intended for patient or veterinary care shall comply with Sections 427.2 through 427.2.3 in addition to the requirements of Chapter 53 of the California Fire Code .

[F] 427.2 Interior Supply Location

Medical gases shall be located in areas dedicated to the storage of such gases without other storage or uses. Where containers of medical gases in quantities greater than the permitted amount are located inside the buildings, they shall be located in a 1-hour exterior room, 1-hour interior room or a gas cabinet in accordance with Section 427.2.1, 427.2.2 or 427.2.3, respectively. Rooms or areas where medical gases are stored or used in quantities exceeding the maximum allowable quantity per control area as set forth in Tables 307.1(1) and 307.1(2) shall be in accordance with Group H occupancies.

[F] 427.2.1 One-Hour Exterior Room

Assembly

A 1-hour exterior room shall be a room or enclosure separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, with a fire-resistance rating of not less than 1 hour. Openings between the room or enclosure and interior spaces shall be provided with self-closing smoke- and draft-control assemblies having a fire protection rating of not less than 1 hour. Rooms shall have not less than one exterior wall that is provided with not less than two vents. Each vent shall have a minimum free air opening of not less than 36 square inches (232 cm2) for each 1,000 cubic feet (28 m3) at normal temperature and pressure (NTP) of gas stored in the room and shall be not less than 72 square inches (465 cm2) in aggregate free opening area. One vent shall be within 6 inches (152 mm) of the floor and one shall be within 6 inches (152 mm) of the ceiling. Rooms shall be provided with not fewer than one automatic fire sprinkler to provide container cooling in case of fire.

Assembly (1)

14-1.3: 1hr, Wood

[F] 427.2.2 One-Hour Interior Room

Assembly

Where an exterior wall cannot be provided for the room, a 1-hour interior room shall be provided and shall be a room or enclosure separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, with a fire-resistance rating of not less than 1 hour. Openings between the room or enclosure and interior spaces shall be provided with self-closing smoke- and draft-control assemblies having a fire protection rating of not less than 1 hour. An automatic sprinkler system shall be installed within the room. The room shall be exhausted through a duct to the exterior. Supply and exhaust ducts shall be enclosed in a 1-hour rated shaft enclosure from the room to the exterior. Approved mechanical ventilation shall comply with the California Mechanical Code and be provided with a minimum rate of 1 cubic foot per minute per square foot (0.00508 m3/s/m2) of the area of the room.

Assembly (1)

14-1.3: 1hr, Wood

[F] 427.2.3 Gas Cabinets

Gas cabinets shall be constructed in accordance with Section 5003.8.6 of the California Fire Code and shall comply with the following:

- Cabinets shall be exhausted to the exterior through a dedicated exhaust duct system installed in accordance with Chapter 5 of the California Mechanical Code.

- Supply and exhaust ducts shall be enclosed in a 1-hour rated shaft enclosure from the cabinet to the exterior. The average velocity of ventilation at the face of access ports or windows shall be not less than 200 feet per minute (1.02 m/s) with a minimum of 150 feet per minute (0.76 m/s) at any point of the access port or window.

- Cabinets shall be provided with an automatic sprinkler system internal to the cabinet.

Section 435 Special Provisions for Licensed 24-Hour Care Facilities in a Group R-2.1, R-3.1, R-4 [SFM]

435.1 Scope

The provisions of this section shall apply to 24-hour care facilities in a Group R-2.1, R-3.1 or R-4 occupancy licensed by a governmental agency.

435.2 General

The provisions in this section shall apply in addition to general requirements in this code.

435.2.1

Restraint shall not be practiced in a Group R-2.1, R-3.1 or R-4 Occupancies.

Exception: Occupancies which meet all the requirements for a Group I-3 Occupancy.

435.2.2

Pursuant to Health and Safety Code Section 13133, regulations of the state fire marshal pertaining to occupancies classified as Residential Facilities (RF) and Residential Care Facilities for the Elderly (RCFE) shall apply uniformly throughout the state and no city, county, city and county, including a charter city or charter county, or fire protection district shall adopt or enforce any ordinance or local rule or regulation relating to fire and panic safety which is inconsistent with these regulations. A city, county, city and county, including a charter city or charter county may pursuant to Health and Safety Code Section 13143.5, or a fire protection district may pursuant to Health and Safety Code Section 13869.7, adopt standards more stringent than those adopted by the state fire marshal that are reasonably necessary to accommodate local climate, geological or topographical conditions relating to roof coverings for Residential Care Facilities for the Elderly.

Exception: Local regulations relating to roof coverings in facilities licensed as a residential care facility for the elderly (RCFE) per Health and Safety Code Section 13133.

435.3 Building Height and Area Provisions

435.3.1

Group R-2.1, R-3.1 and R-4 shall be constructed in accordance with Table 504.3.

435.3.2 Limitations Six or Less Clients

Group R-3.1 occupancies where nonambulatory clients are housed above the first story, having more than two stories in height or having more than 3,000 square feet (279 m2) of floor area above the first story shall not be of less than one-hour fire-resistance-rated construction throughout.

In Group R3.1 occupancies housing a bedridden client, the client sleeping room shall not be located above or below the first story.

Exception: Clients who become bedridden as a result of a temporary illness as defined in Health and Safety Code Sections 1566.45, 1568.0832 and 1569.72. A temporary illness is an illness, which persists for 14 days or less. A bedridden client may be retained in excess of the 14 days upon approval by the Department of Social Services and may continue to be housed on any story in a Group R-3.1 occupancy classified as a licensed residential facility.

Every licensee admitting or retaining a bedridden resident shall, within 48 hours of the resident's admission or retention in the facility, notify the local fire authority with jurisdiction of the estimated length of time the resident will retain his or her bedridden status in the facility.

435.3.3 Limitations Seven or More Clients

Group R-4 occupancies where nonambulatory clients are housed above the first story and there is more than 3,000 square feet (279 m2) of floor area above the first story or housing not more than 16 clients above the first story shall be constructed of not less than one-hour fire-resistance-rated construction throughout.

435.3.4 Nonambulatory Elderly Clients

Group R-4 occupancies housing nonambulatory elderly clients shall be of not less than one-hour fire-resistance-rated construction throughout.

435.4 Type of Construction Provisions

435.4.1

Group R-2.1, occupancies are not permitted in nonfire-resistance-rated construction, see Health and Safety Code Section 13131.5.

435.5 Fire-Resistance-Rated Construction Provisions

435.5.1 Smoke Barriers Required

Group R-2.1 and R-4 occupancies licensed as a Residential Care Facility (RCF) with individual floor areas over 6,000 square feet (557 m2) per floor, shall be provided with smoke barriers, constructed in accordance with Section 709.

Group R-2.1 occupancies housing bedridden clients shall be provided with smoke barriers constructed in accordance with Section 709 regardless of the number of clients.

When smoke barriers are required, the area within a smoke compartment shall not exceed 22,500 square feet (2090 m2) nor shall its travel distance exceed 200 feet (60 960 mm). Such smoke barriers shall divide the floor as equally as possible.

435.5.2 Smoke Partitions

Group R-2.1 occupancies where smoke partitions are required, framing shall be covered with noncombustible materials having an approved thermal barrier with an index of not less than 15 in accordance with FM 4880, UL 1040, NFPA 286 or UL 1715.

435.5.3 Independent Egress

At least two means of egress shall be provided from each smoke compartment created by smoke barriers. Means of egress may pass through adjacent compartments provided it does not return through the smoke compartment from which means of egress originated. Smoke compartments that do not contain an exit shall be provided with direct access to not less than two adjacent smoke compartments.

435.6 Interior Finish Provisions

435.6.1 Interior Wall and Ceiling Finish

Group R-3.1 occupancies housing a bedridden client shall comply with interior wall and ceiling finish requirements specified for Group I-2 occupancies in Table 803.13.

435.6.2 Safety Padding

Padding material used on walls, floors and ceilings in Group I and R-2.1 occupancies shall be of an approved type tested in accordance with the procedures established by State Fire Marshal Standard 12-8-100, Room Fire Test for Wall and Ceiling Materials, California Code of Regulations, Title 24, Part 12.

435.7 Fire Protection System Provisions

435.7.1 Automatic Sprinkler Systems in Group R-2.1, R-3.1 and R-4 Occupancies

An automatic sprinkler system shall be installed where required in Section 903.

435.7.2 Fire Alarm Systems in Group R-2.1 and R-4 Occupancies

An approved fire alarm system shall be installed where required in Section 907.

435.7.3 Smoke Alarms in Groups R-2.1, R-3.1 and R-4 Occupancies

Smoke alarms shall be installed where required in Section 907.2.11.2.

435.7.4 Hearing Impaired

See Section 907.5.2.3.4.

435.8 Means of Egress Provisions

435.8.1 General

In addition to the general means of egress requirements of Chapter 10, this section shall apply to Group R-2.1, R-3.1 and R-4 occupancies.

435.8.2 Number of Exits

435.8.2.1

Group R-2.1, R-3.1 and R-4 occupancies shall have a minimum of two exits.

Exception: Ancillary use areas or occupancies shall have egress as required by Section 1021.

435.8.3 Egress Arrangements

435.8.3.1

Egress through adjoining dwelling units shall not be permitted.

435.8.3.2 Group R-3.1 Occupancies Housing Non- Ambulatory Clients

In a Group R-3.1 occupancy, bedrooms used by nonambulatory clients shall have access to at least one of the required exits which shall conform to one of the following:

- Egress through a hallway or area into a bedroom in the immediate area which has an exit directly to the exterior and the corridor/hallway is constructed consistent with the dwelling unit interior walls. The hallway shall be separated from common areas by a solid wood door not less than 13/8 inch (35 mm) in thickness, maintained self-closing or shall be automatic closing by actuation of a smoke detector installed in accordance with Section 716.2.6.

- Egress through a hallway which has an exit directly to the exterior. The hallway shall be separated from the rest of the house by a wall constructed consistent with the dwelling unit interior walls and opening protected by a solid wood door not less than 13/8 inch (35 mm) in thickness, maintained self-closing or shall be automatic closing by actuation of a smoke detector installed in accordance with Section 716.2.6.

- Direct exit from the bedroom to the exterior shall be of a size as to permit the installation of a door not less than 3 feet (914 mm) in width and not less than 6 feet 8 inches (2032 mm) in height. When installed, doors shall be capable of opening at least 90 degrees and shall be so mounted that the clear width of the exit way is not less than 32 inches (813 mm).

- Egress through an adjoining bedroom which exits to the exterior.

435.8.3.3 Group R-3.1 Occupancies Housing Only One Bedridden Client

In Group R-3.1 occupancies housing a bedridden client and not provided with an approved automatic sprinkler system, all of the following shall apply:

- In Group R-3.1 occupancies housing a bedridden client, a direct exit to the exterior of the residence shall be provided from the client sleeping room.

- Doors to a bedridden client's sleeping room shall be of a self-closing, positive latching 1-3/8 inch solid wood door. Such doors shall be provided with a gasket so installed as to provide a seal where the door meets the jam on both sides and across the top. Doors shall be maintained self-closing or shall be automatic closing by actuation of a smoke alarm in accordance with Section 716.2.6.

- Group R-3.1 occupancies housing a bedridden client, shall not have a night latch, dead bolt, security chain or any similar locking device installed on any interior door leading from a bedridden client's sleeping room to any interior area such as a corridor, hallway and or general use areas of the residence in accordance with Chapter 10.

- The exterior exit door to a bedridden client's sleeping room shall be operable from both the interior and exterior of the residence.

- Every required exit doorway from a bedridden client sleeping room shall be of a size as to permit the installation of a door not less than 3 feet (914 mm) in width and not less than 6 feet 8 inches (2032 mm) in height. When installed in exit doorways, exit doors shall be capable of opening at least 90 degrees and shall be so mounted that the clear width of the exit way is not less than 32 inches (813 mm).

  - Note: A sliding glass door can be used as an exterior exit doorway as long as it is operable from the inside and outside and the clear width of the exit way is not less than 32 inches (813 mm).

435.8.3.4 Intervening Rooms

A means of exit shall not pass through more than one intervening room. A means of egress shall not pass through kitchens, storerooms, closets, garages or spaces used for similar purposes.

Exception: Kitchens which do not form separate rooms by construction.

435.8.4 Corridors

435.8.4.1

Unless specified by Section 435.8.4, corridors serving Group R-2.1 and Group R-4 occupancies shall comply with Section 1020.1.

In Group R-2.1 occupancies provided with fire sprinklers throughout and which are required to have rated corridors, door closers need not be installed on doors to client sleeping rooms.

435.8.4.2

The minimum clear width of a corridor shall be as follows:

- Group R-2.1 occupancies shall have 60 inches (1524 mm) on floors housing nonambulatory clients and 44 inches (1118 mm) on floors housing only ambulatory clients.

- Group R-4 occupancies shall have 44 inches (1118 mm) on floors housing clients.

Exceptions:

- Corridors serving an occupant load of 10 or less shall not be less than 36 inches (914 mm) in width.

- Corridors serving ambulatory persons only and having an occupant load of 49 or less shall not be less than 36 inches (914 mm) in width.

435.8.4.3

In a Group R-2.1 and Group R-4 occupancies having smoke barriers, cross-corridor doors in corridors 6 feet (1829 mm) or less in width shall have, as a minimum, a door 36 inches (914 mm) in width.

435.8.5 Changes in Level

In Group R-3.1 occupancies housing nonambulatory clients interior changes in level up to 0.25 inch (6 mm) may be vertical and without edge treatment. Changes in level between 0.25 inch (6 mm) and 0.5 inch (12.7 mm) shall be beveled with a slope no greater than 1 unit vertical in 2 units horizontal (50 percent slope). Changes in level greater than 0.5 inch (12.7 mm) shall be accomplished by means of a ramp.

435.8.6 Stairways

435.8.6.1

Group R-2.1 and Group R-4 occupancies housing more than six nonambulatory clients above the first floor shall be provided with two vertical exit enclosures. Stairway enclosures shall be in compliance with Section 1023. Exceptions to Section 1023 shall not apply in facilities licensed as a 24-hour care facility.

435.8.6.2

Group R-3.1 occupancies may continue to use existing stairways (except for winding and spiral stairways which are not permitted as a required means of egress) provided the stairs have a maximum rise of 8 inches (203 mm) with a minimum run of 9 inches (229 mm). The minimum stairway width may be 30 inches (762 mm).

435.8.7 Floor Separation

Group R-3.1 occupancies with non-ambulatory clients housed above the first floor shall be provided with a non-fire resistance constructed floor separation at stairs which will prevent smoke migration between floors. Such floor separation shall have equivalent construction of 0.5 inch (12.7 mm) gypsum wallboard on one side of wall framing.

Exceptions:

- Occupancies with at least one exterior exit from floors occupied by clients.

- Occupancies provided with automatic fire sprinkler systems complying with Chapter 9.

435.8.7.1 Doors Within Floor Separations

Doors within such floor separations shall be tight fitting solid wood at least 13/8 inches (35 mm) in thickness. Door glazing shall not exceed 1296 square inches (32 918 mm2) with no dimension greater than 54 inches (1372 mm). Such doors shall be positive latching, smoke gasketed and shall be automatic-closing by smoke detection.

435.8.8 Fences and Gates

Grounds of a Residential Care Facility for the Elderly serving Alzheimer clients may be fenced and gates therein equipped with locks, provided safe dispersal areas are located not less than 50 feet (15 240 mm) from the buildings. Dispersal areas shall be sized to provide an area of not less than 3 square feet (0.28 m2) per occupant. Gates shall not be installed across corridors or passageways leading to such dispersal areas unless they comply with egress requirements.

435.8.9 Basement Exits

One exit is required to grade level when the basement is accessible to clients.

435.8.10 Delayed Egress Locks

See Section 1010.2.13.

435.9 Request for Alternate Means of Protection for Facilities Housing Bedridden Clients

Request for alternate means of protection shall apply to Sections 435 through 435.9. Request for approval to use an alternative material, assembly or materials, equipment, method of construction, method of installation of equipment or means of protection shall be made in writing to the local fire authority having jurisdiction by the facility, client or the client's authorized representative. Sufficient evidence shall be submitted to substantiate the need for an alternate means of protection.

The facility, client or the client's representative or the local fire authority having jurisdiction may request a written opinion from the State Fire Marshal concerning the interpretation of the regulations promulgated by the State Fire Marshal for a particular factual dispute. The State Fire Marshal shall issue the written opinion within 45 days following the request. Approval of a request for use of an alternative material, assembly or materials, equipment, method of construction, method of installation of equipment or means of protection made pursuant to this section shall be limited to Group R-3.1 occupancies housing a bedridden client. Approvals made by the local fire authority having jurisdiction and the written opinion by the State Fire Marshal shall be applicable only to the requesting facility and shall not be construed as establishing any precedent for any future request by that facility or any other facility.

435.10 Temporarily Bedridden Clients

Clients who become temporarily bedridden as defined in Health and Safety Code Section 1569.72, as enforced by the Department of Social Services, may continue to be housed on any story in Group R-2.1, R-3.1 or R-4 occupancies classified as Residential Care Facilities for the Elderly (RCFE). Every Residential Care Facility for the Elderly (RCFE) admitting or retaining a bedridden resident shall, within 48 hours of the resident's admission or retention in the facility, notify the local fire authority with jurisdiction of the estimated length of time the resident will retain his or her bedridden status in the facility.

435.11 Group R-2.1, R-3.1, R-4

[SFM] Buildings housing protective social care need not be of 1-hour fire-resistive construction when not more than two stories in height. In no case shall individual floor areas exceed 3,000 square feet (279 m2). The fire-resistive protection of the exterior walls shall not be less than 1 hour where such walls are located within 5 feet (1524 mm) of the property line. Openings within such walls are not permitted. Openings in exterior nonrated walls need not be protected.

Section 436 Group I-4 [SFM]

436.1 Group I-4 Special Provisions

Diagram

Rooms classified as Group I-4 shall not be located above or below the first story.

Exceptions:

- Basements or stories having floor levels located within 4 feet (1219 mm), measured vertically, from adjacent ground level at the level of exit discharge, provided the basement or story has exterior exit doors at that level.

- Group I-4 child-care center or adult day care may be located above the first story in buildings of Types II-A, III-A, IV-A, IV-B and IV-C construction, subject to the limitation of Section 503 when:

  - Group I-4 child-care centers with children under the age of seven or containing more than 12 children per story shall not be located above the fourth floor; and

  - The entire story in which the Group I-4 child-care center or adult day care is located is equipped with an approved manual fire alarm and automatic smoke-detection system. (See the California Fire Code.) Actuation of an initiating device shall sound an audible alarm throughout the entire story. When a building fire alarm system is required by other provisions of this code or the Fire Code, the alarm system shall be connected to the building alarm system. An approved alarm signal shall sound at an approved location in the Group I-4 facility to indicate a fire alarm or sprinkler flow condition in other portions of the building; and

  - Group I-4 child-care center or adult day care, if more than 1,000 square feet (92.9 m2) in area, is divided into at least two compartments of approximately the same size by a smoke barrier with door openings protected by smoke- and draft-control assemblies having a fire-protection rating of not less than 20 minutes. Smoke barriers shall have a fire-resistive rating of not less than one hour. In addition to the requirements of Section 508.3.3, occupancy separations between Group I-4 child-care center or adult day care and other occupancies shall be constructed as smoke barriers. Door openings in the smoke barrier shall be tightfitting, with gaskets installed as required by Section 710, and shall be automatic closing by actuation of the automatic sprinklers, fire alarm or smoke-detection system.

  - Each compartment formed by the smoke barrier has not less than two exits or exit access doors, one of which is permitted to pass through the adjoining compartment; and

  - Where two or more exits or exit access are required at least one shall not share a common path of travel. The egress system shall comply with the requirements of Section 709 for smoke barriers.

  - The building is equipped with an automatic sprinkler system throughout.

UpCodes Diagram (1)

Common Path of Egress Travel

436.1.1 Egress

Rooms used for Group I-4 child care or adult day care on the first floor shall have one exit door directly to the exterior.

Exception: One-hour rated corridors with a minimum width of 60 inches.

Section 437 Reserved

Section 438 Reserved

Section 439 Road Tunnels, Bridges and Other Limited-Access Highways [SFM]

439.1 General

Road tunnels, bridges and other limited-access highways that are state owned shall comply with NFPA 502.

Section 440 Horse Racing Stables [SFM]

440.1

For automatic sprinkler and fire alarm system requirements applying to each building, barn or structure which is used by an association regulated by the California Horse Racing Board for the stabling of horses or human habitation, and the stable area grounds, including any additional location where any excess horses are stabled see Title 4, Division 4, Article 17, Section 1927.

Section 441 Pet Kennels and Pet Boarding Facilities [SFM]

441.1

These regulations shall apply to every building or fire area in which a pet boarding facility operates, as defined in Health and Safety Code Section 122380, or a pet dealer, as defined in Health and Safety Code Section 122125, maintains a kennel.

441.2 Automatic Sprinkler System

An approved automatic sprinkler system complying with California Fire Code Section 903 shall be installed.

Exception: Where a fire alarm system that is connected to a central reporting station that alerts the local fire department in case of fire.

Section 442 Combustion Engines and Gas Turbines [SFM]

442.1 General

The installation of combustion engines and gas turbines shall be in accordance with NFPA-37 and this chapter.

442.2 Separation

442.2.1 Construction

Every room in which is installed a combustion engine or gas turbine shall be separated from the remainder of the building by not less than a one-hour fire barrier.

442.2.2 Exterior Openings

When doors, windows or louvered openings are located below openings in another story or less than 10 feet (3048 mm) from doors, windows or louvered openings of the same building, they shall be protected by a fire assembly having a 3/4-hour rating. Such fire assemblies shall be fixed, automatic or self-closing.

442.2.2.1 Interior Openings

In other than buildings housing Group I and R-2.1 occupancies, interior openings shall be allowed in buildings protected by an automatic fire sprinkler system throughout.

442.2.3 Location

Combustion engines and gas turbines used for emergency power shall not be located in a room or area used for any other purpose other than equipment and controls related to the generation and distribution of emergency power.

442.2.4 Special Hazards

The handling and use of flammable or combustible liquids shall comply with the California Fire Code.

Section 443 Fixed Guideway Transit and Passenger Rail Systems [SFM]

443.1 General

443.1.1 Scope

The provisions of this section and NFPA 130 shall apply to buildings or structures defined as stations for fixed guideway transit and passenger rail systems and shall supersede other similar requirements in other sections of this code.

- Note: See Chapter 35 for California Amendments to NFPA 130.

443.2 Special Provisions

443.2.1 Automatic Sprinkler System

See Section 903.2.17.1.

443.2.2 Station Guideway Deluge System

See Section 903.2.17.2.

443.2.3 Standpipe Systems

See Section 905.3.11.

443.2.4 Fire Alarm and Communication Systems

See Section 907.2.26.

443.2.5 Emergency Ventilation Control

Emergency ventilation systems shall comply with this section and NFPA 130.

443.2.5.1

Emergency ventilation systems shall be supervised and/or controlled in all operating modes locally (motor control center and/or fan unit) and remotely at both the Operations Control Center and the station Fire Command Center.

443.2.5.2

Fan running shall be provided by sensing devices for each fan for operation in both the supply and exhaust directions.

443.2.5.3

Trouble status signals shall be annunciated in the local control room. A summarized trouble signal shall be annunciated at Operations Control Center and Fire Command Center.

Section 444 Explosives [SFM]

[Section 444 has been repealed and replaced by the adoption of California Fire Code Chapter 56.]

Section 445 Reserved

Section 446 Winery Caves [SFM]

446.1 Scope

The use of subterranean space for winery facilities in natural or manmade caves shall be in accordance with this section.

446.2 Definitions

446.3 General

For definitions of ASSEMBLY, FIRE APPLIANCE and NONCOMBUSTIBLE, see Chapter 2.

446.4 Limited Application

For the purpose of Section 446, certain terms are defined as follows:

Type 1 Winery Caves

are natural or manmade caves used solely for storage and/or processing of wine at a winery facility. Type 1 winery caves are not accessible to the public.

Type 2 Winery Caves

are natural or manmade caves used for the storage and/or processing of wine at a winery facility. Type 2 winery caves are accessible to the public on guided tours only.

Type 3 Winery Caves

are natural or manmade caves used for the storage and/or processing of wine at a winery facility. Type 3 winery caves are accessible to the public on guided tours and contain assembly use areas.

446.5 Permits

For permits to operate Type 2 and 3 winery caves, see Section 105.

446.6 Fire Apparatus Access Roads

Fire apparatus access roads shall be constructed and maintained in accordance with the California Fire Code, Section 503.

446.7 Construction Requirements

446.7.1 Allowable Area

The area of winery caves shall not be limited if constructed entirely of noncombustible materials. Winery caves constructed with combustible materials shall be limited in area so that no point is more than 150 feet (45 720 mm) from an exit.

446.7.2 Interior Construction

The walls and ceilings of winery caves shall not contain hidden or concealed spaces.

446.8 General Requirements

446.8.1 Public Tours

Tours for the public shall be continuously guided by staff knowledgeable in the location of exits and the use of emergency notification devices.

446.8.2 Standby Personnel

Per the California Fire Code, Section 2404.20, when, in the opinion of the fire chief, it is essential for public safety, the owner, agent or lessee shall employ one or more qualified persons, as required and approved by the chief, to be on duty at such place. Such individuals shall be in uniform or otherwise easily identifiable.

Standby personnel shall be subject to the fire chief's orders at all times when so employed and shall remain on duty during the times such places are open to the public or when such activity is being conducted.

Before the start of any activity requiring standby personnel, such individuals shall:

- Inspect the required fire appliances to ensure they are in the proper place and in good working order.

- Inspect all exits to verify accessibility and proper operation.

While on duty, such individuals shall not be required or permitted to perform any duties other than those specified by the fire chief.

446.8.3 Open-Flame Devices

The use of candles and other open-flame devices shall be in accordance with California Fire Code Section 308.1.7.

446.9 Portable Fire Extinguishers and Other Fire Appliances

Portable fire extinguishers shall be located to be readily accessible. Its type, location and spacing throughout the facility shall be in accordance with the provisions of Title 19, Chapter 3 and California Fire Code Section 906.1. Other fire appliances shall be maintained at the site as required by the fire chief.

446.10 Fire Alarm Systems

An approved manual fire alarm system conforming with the provisions of the California Fire Code, Section 907.2.1 shall be provided in all Type 3 winery caves.

446.11 Exits

446.11.1 Distribution

Exits shall be located remotely from each other and arranged to minimize any possibility that more than one may be blocked off by any one fire or other emergency condition.

446.11.2 Number

Winery caves shall be provided with a minimum of two exits.

Assembly areas of Type 3 winery caves shall be provided with exits as required by the California Building Code for Group A Occupancies.

446.12 Exit Illumination

446.12.1 General

Exits shall be illuminated to a minimum intensity of not less than 1 foot-candle (10.76 lx) at floor level whenever the winery cave is occupied. Fixtures providing exit illumination shall be supplied from a dedicated circuit or source of power used only for exit illumination.

446.12.2 Separate Sources of Power

The power supply for exit illumination may be provided by the premises' wiring system. In the event of its failure, illumination shall be automatically provided from an emergency system in Types 2 and 3 winery caves. Emergency systems shall be supplied from storage batteries or an on-site generator set, and the system shall be installed in accordance with the requirements of the California Electrical Code.

446.13 Exit Signs

Exit signs shall be installed at required exits and where otherwise necessary to clearly indicate the exits from assembly areas in Type 3 winery caves.

446.14 Maximum Occupant Load

Occupant load requirements in the assembly areas of Type 3 winery caves shall be in accordance with Section 1004.

446.15 Seating Arrangements

Seating arrangements in the assembly areas of Type 3 winery caves shall be in accordance with California Fire Code, Section 1028.9.

Section 447 Reserved

Section 448 Reserved

Section 449 Public Libraries [SL and SFM]

Public libraries funded from the California Library Construction and Renovation Act of 1988.

449.1 Automatic Sprinkler System

Automatic sprinkler systems shall be installed in:

- New facilities, including additions;

- Existing facilities to which a project adds the lesser of 5,000 square feet (465 m2) or 10 percent of the size of the existing facility, if the existing facility does not already have an automatic sprinkler system.

449.2 System Monitoring Requirement

All fire protection systems shall be monitored by a fire alarm supervising station in accordance with the NFPA 72.

449.3 Book Return Slots

Any interior book return with a slot piercing the exterior wall shall have a separate sprinkler head and be enclosed in fire-rated construction.

449.4 Automatic Sprinkler and Extinguishing Systems

For public libraries constructed with funds awarded under the California Reading and Literacy Improvement and Public Library Construction and Renovation Bond Act of 2000:

- Fire sprinkler system requirement. All libraries funded for new construction, including additions, shall have automatic fire sprinkler systems installed.

- Fire sprinkler system requirement for renovations of existing facilities. If there is no automatic fire sprinkler system in the existing facility, grant recipients shall be required to install a fire sprinkler system throughout the existing facility.

- Fire sprinkler system types. The grant recipient may choose, on approval by the local fire authority, from wet-pipe, dry-pipe or pre-action systems, utilizing listed standard, early suppression fast response (ESFR), or on/off type sprinkler heads.

- Book return rooms and slots. Book return rooms with slots in exterior walls shall have an automatic sprinkler head and be of approved fire-resistive construction. Book return slots and book drops shall have an additional automatic sprinkler head when shielded from the room sprinkler head.

- System monitoring requirement. All fire protection systems shall be monitored by a fire alarm supervising station in accordance with the National Fire Protection Association (NFPA) 72.

- Alternate fire-extinguishing systems for specialized areas. When approved by the fire authority having jurisdiction, other types of approved automatic fire-extinguishing systems may be utilized as an alternate to sprinklers in the following areas: rare book rooms, central computer rooms and telecommunication rooms.

- Automatic sprinkler system plan requirement. Fire sprinkler system drawings shall use the furniture plan as a background for coordination with furniture and book stack location and height.

Section 450 Group C [SFM]

450.1 Group C Occupancies Defined

450.1.1 Organized Camps

For the purposes of these regulations, Group C Occupancies shall mean "organized camps" as defined in Section 18897, Health and Safety Code.

450.1.1.1 Description

An organized camp is a site with programs and facilities established for the primary purpose of providing an outdoor group living experience with social, spiritual, educational or recreational objectives, for five days or more during one or more seasons of the year.

The term "organized camp" does not include a motel, tourist camp, trailer park, resort, hunting camp, auto court, labor camp, penal or correctional camp, child-care institution or home-finding agency nor does it include any charitable or recreational organization which complies with the rules and regulations for recreational trailer parks provided for by Section 18301 (b), Health and Safety Code.

450.1.2 Tents and Tent Structures

For the purpose of this chapter, a tent or tent structure is defined as any shelter of which 25 percent or more of the walls or roof, or both, are constructed of, or covered or protected by, a canvas or any other fabric material.

450.2 Purpose and Intent

The provisions of this section are established to provide fire and life safety in organized camps, but at the same time preserve the basic concept of outdoor living. It is the intent of this section that organized camps shall be considered as a separate and distinct occupancy.

450.3 Basic Building and Structures

450.3.1 Building Classification

Every building or structure shall be classified into the occupancy group they most nearly resemble and be constructed in accordance with appropriate occupancy requirements specified in this part.

Exceptions:

- Tents, tent structures, and buildings and structures that do not exceed 25 feet (7620 mm) in any lateral dimension and where such building or structure is not more than one story.

- For fire safety, buildings or structures on the premises of an organized camp which are used for sleeping purposes, regardless of their similarity to other occupancy groups, shall conform to the provisions of Sections 450.4, 450.5, 450.6 and 450.7.

- For fire safety, buildings and structures which are not used for sleeping purposes shall conform to the provisions of Section 450.7, which shall supersede any similar provisions contained in this part.

450.3.2 Occupant Load

The living shelter whether a building, structure, tent and tent structure, or cabin, shall provide a minimum of 30 square feet (2.8 m2) of superficial floor area per person for single-tier bed units, and 20 square feet (1.9 m2) of superficial floor area per person for two-tier bed units. More than two tiers per bed unit are prohibited. There shall be at least 3 feet (914 mm) of lateral distance between beds.

Exception: Intermittent short-term organized camps are not required to provide shelter facilities but, if provided, they shall comply with this section.

450.4 General

450.4.1 Buildings Intended for Sleeping

Buildings and structures used or intended for sleeping purposes which do not exceed any one of the limitations set forth below shall conform to the provisions of Sections 450.5 and 450.7.

- One story in height

- Twenty-five feet (7620 mm) in any lateral dimension

Exception: This provision shall not apply to buildings or structures conforming to construction provisions of this section in effect prior to January 1, 1985.

- Maximum housing of 12 persons

450.4.2 Limitations

Buildings and structures used or intended for sleeping purposes, including those so used in whole or in part by staff personnel, and which exceed any one of the limitations set forth in Section 450.4.1, shall conform to the provisions of Sections 450.5 and 450.7.

Exception: Buildings or structures used exclusively for living and sleeping purposes by resident custodial or caretaker personnel only may be constructed in accordance with the provisions of these regulations for a Group R, 3 Occupancy.

450.5 Special Buildings, Tents and Tent Structures

450.5.1 Special Buildings

In addition to the provisions of Section 450.7, special buildings conforming to the limitations specified in Section 450.4.1 shall conform to the following:

- The flame-spread end-point rating of all interior finish materials shall not exceed 200.

- Every room or area housing more than eight persons shall be provided with not less than two approved exits, each of which shall be direct to the exterior and shall not be less than 32 inches (813 mm) in clear width and 6 feet 8 inches (2032 mm) in height. Rooms or areas housing eight or less persons shall be provided with at least one such exit direct to the exterior.

- Every exit door shall be openable from the inside without the use of any key, special knowledge or effort.

- Exit doors need not be hung to swing in the direction of exit travel. Where exit doors are hung to swing in the direction of exit travel, a landing conforming to the provisions of Section 1010.1.5 shall be provided.

- When the distance (measured vertically) between the ground level and the floor level exceeds 8 inches (203 mm), a stairway from each exit shall be provided. Steps shall have a rise of not more than 8 inches (203 mm) and a run of not less than 9 inches (229 mm). Such stairway shall be at least as wide as the door it serves.

Exception: In lieu of a stairway, a ramp having a slope of not more than 1 foot (305 mm) of rise for each 8 feet (2438 mm) of run may be provided.

- When the floor level at any door opening of any building or structure is more than 30 inches (762 mm) above the adjacent ground level, handrails or guardrails shall be provided on the landing, balcony or porch, and on every stairway or ramp to ground level.

- Buildings and structures or groups of buildings and structures shall be separated from each other by not less than 10 feet (3048 mm).

Exception: This section shall not apply to existing buildings and structures of Group C Occupancies.

450.5.2 Tents and Tent Structures

In addition to the provisions of Section 450.7, tents and tent structures, or groups thereof, shall conform to the provisions of Section 450.5, except as follows:

- Regardless of any other provisions of this section, heating of tents and tent structures shall be prohibited unless written permission is obtained from the fire chief.

- All canvas or other fabric material shall be treated and maintained in a flame-retardant condition.

Exceptions:

  - Tents in existence prior to January 1, 1979, provided the following conditions are met:

    - Tents shall not exceed 80 square feet (7.4 m2) in area.

    - No electrical devices, except flashlights, are installed or used in the tents.

    - Tents are not located closer than 30 feet (9144 mm) to any open fire.

    - Smoking is prohibited in the tents.

    - All other applicable provisions of this article are met.

  - Canvas or materials used exclusively to protect windows and similar openings in walls.

  - Canvas or materials used as a windbreak enclosure of not more than three sides and open to the sky.

Note: It is not the intent of Section 450.5.2 that strict adherence to the width and height requirements of exit openings be enforced for exits from tents.

450.6 Building and Structures for Sleeping

Buildings and structures, or portions thereof, used or intended for sleeping purposes and which exceed the height, area or capacity limitations specified in Section 450.4.1 shall conform to the provisions of this section.

450.6.1 Area, Height and Type of Construction

Buildings and structures, or portions thereof, shall not exceed the limits of area, height and type of construction specified in these regulations for a Group R-2.1 occupancy. Such buildings and structures shall not be of less than one-hour fire-resistive construction throughout.

450.6.2 Location on Property

The fire-resistive protection of exterior walls and openings, as determined by location on property, shall be in accordance with the provisions of these regulations for a Group R-2.1 occupancy.

450.6.3 Exits

Stairs, exits and smoke-proof enclosures shall be provided in accordance with the provisions of Chapter 10.

450.6.4 Enclosure of Vertical Openings

Exits shall be enclosed as specified in Chapter 10. Elevator shafts, vent shafts and other vertical openings shall be enclosed and enclosures shall be as set forth in Chapter 7.

450.6.5 Fire-Extinguishing Systems

Automatic fire-extinguishing systems, standpipes and basement pipe inlets shall be installed when and as specified in Chapter 9 for buildings, based on the occupancy they most nearly resemble.

450.6.6 Automatic Fire Alarm System

See Section 907.

450.7 Special Requirements

The provisions of this section shall apply to the premises and to all buildings and structures of all organized camps.

450.7.1 Electrical

The installation of all electrical wiring shall conform to the applicable provisions of the California Electrical Code.

450.7.2 Heating Equipment

Heating equipment, and the installation thereof, shall conform to the provisions of the California Mechanical Code.

450.7.3 Motion Picture Booths

Motion picture machine booths shall conform to the requirements of Section 409.

450.7.4 Interior Finish

Interior finish shall conform to the requirements of Chapter 8, except as permitted in Section 450.5.1, Item 1.

450.7.5 Heater Room Openings

All exterior openings in rooms containing central heating equipment, low-pressure boilers or water-heating boilers used as part of the heating system, if located below openings in another story, or if less than 10 feet (3048 mm) from other doors or windows of the same building, shall be protected by a fire assembly having a three-fourths-hour fire-resistive rating. Such fire assemblies shall be fixed, automatic or self-closing.

Exception: The requirement for three-fourths-hour fire assembly protection of openings may be deleted if the entire room is protected by an automatic sprinkler system conforming to the provisions of Section 903.

450.7.6 Heating Rooms

Every room containing central-heating equipment, low-pressure boiler or water-heating boiler used as part of the heating system shall be separated from the rest of the building by a one-hour fire-resistive fire barrier with all openings protected as set forth in Section 707.6.

Exceptions:

- Boilers or central heating plants where the largest piece of fuel equipment does not exceed 400,000 Btu per hour (135 kW) input.

- When any such opening is protected by a pair of fire doors, the inactive leaf shall be normally secured in the closed position and shall be openable only by use of a tool. An astragal shall be provided and the active leaf shall be self-closing.

450.7.7 Exits

For purposes of determining occupant load for exit requirements, see Section 450.3.2.

450.7.8 Liquefied Petroleum Gas

The construction and installation of all tanks, cylinders, equipment and systems used or intended for use in conjunction with any liquefied petroleum gas shall conform to the provisions of the California Mechanical Code and the California Fire Code.

450.7.9 Air-Conditioning and Ventilation Systems

Heating units used as an integral part of an air-conditioning and ventilation system shall be installed in accordance with Sections 450.7.2, 450.7.3 and 450.7.6.

450.8 Camp Fire Alarm

Every organized camp shall provide and maintain a device or devices suitable for sounding a fire alarm. Such device or devices may be of any type acceptable to the enforcing agency provided they are distinctive in tone from all other signaling devices or systems and shall be audible throughout the camp premises. When an automatic fire alarm system is provided, as required by Section 450.6.6, all signaling devices required by this section shall be of the same type as that used in the automatic system.

Section 451 Reserved

Section 452 School Facilities for Kindergarten Through 12th Grade and Group E Child Care

452.1 General Provisions

School facilities for Kindergarten through 12th grade and Group E child care shall comply with the provisions of this section and other applicable provisions of this code including requirements for specific occupancies.

452.1.1 Location on Property

All buildings housing Group E occupancies shall front directly on a public street or an exit discharge not less than 20 feet (6096 mm) in width. The exit discharge to the public street shall be a minimum 20-foot-wide (6096 mm) right-of-way, unobstructed and maintained only as access to the public street. At least one required exit shall be located on the public street or on the exit discharge.

452.1.2 Separate Means of Egress Systems Required

Every room with an occupant load of 300 or more shall have one of its exits or exit-access doorways lead directly into a separate means of egress system that consists of not less than two paths of exit travel which are separated by a smoke barrier in accordance with Section 709 in such a manner to provide an atmospheric separation that precludes contamination of both paths of exit travel by the same fire. Not more than two required exits or exit-access doorways shall enter into the same means of egress system.

452.1.3 Fences and Gates

School grounds may be fenced and gates therein may be equipped with locks, provided that safe dispersal areas based on 3 square feet (0.28 m2) per occupant are located between the school and the fence. Such required safe dispersal areas shall not be located less than 50 feet (15 240 mm) from school buildings.

Every public and private school shall conform with Section 32020 of the Education Code which states:

The governing board of every public school district, and the governing authority of every private school, which maintains any building used for the instruction or housing of school pupils on land entirely enclosed (except for building walls) by fences of walls, shall, through cooperation with the local law enforcement and fire-protection agencies having jurisdiction of the area, make provision for the erection of gates in such fences or walls. The gates shall be of sufficient size to permit the entrance of the ambulances, police equipment and firefighting apparatus used by the law enforcement and fire-protection agencies. There shall be no less than one such access gate and there shall be as many such gates as needed to assure access to all major buildings and ground areas. If such gates are to be equipped with locks, the locking devices shall be designed to permit ready entrance by the use of the chain or bolt-cutting devices with which the local law enforcement and fire-protection agencies may be equipped.

452.1.4 Special Provisions

Rooms used by kindergarten, first- or second-grade pupils, and Group E child care, shall not be located above or below the first story.

Exceptions:

- Kindergarten, first- or second-grade pupils, or Group E child care may be located in basements or stories having floor levels located within 4 feet (1219 mm), measured vertically, from the adjacent ground level at the level of exit discharge, provided the basement or story has exterior exit doors at that level.

- In buildings equipped with an automatic sprinkler system throughout, rooms used for kindergarten, first- and second-grade children or for Group E child-care purposes may be located on the second story, provided there are at least two exterior exit doors, or other egress systems complying with Section 1020 with two exits, for the exclusive use of such occupants. Egress systems for the exclusive use of such occupants shall be maintained until exit discharge at grade is attained.

- Group E day-care facilities may be located above the first story in buildings of Type I-A, I-B, II-A, III-A, IV-A, IV-B and IV-C construction, subject to the limitation of Section 503 when:

  - Facilities with children under the age of seven or containing more than 12 children per story shall not be located above the fourth floor; and

  - The entire story in which the day-care facility is located is equipped with an approved manual fire alarm and automatic smoke-detection system. Actuation of an initiating device shall sound an audible alarm throughout the entire story.

When a building fire alarm system is required by other provisions of this code, the alarm system shall be interconnected and sound the day-care fire alarm system; and

  - The day-care facility, if more than 1,000 square feet (92.9 m2) in area, is divided into at least two compartments of approximately the same size by a smoke barrier in accordance with Section 709. In addition to the requirements of Section 508, occupancy separations between day-care and other occupancies shall be constructed as smoke barriers. Door openings in the smoke barrier shall be tight fitting, with gaskets installed as required by Section 716.5.3.1 and shall be automatic closing by actuation of the fire sprinklers, fire alarm or smoke detection system; and

  - Each compartment formed by the smoke barrier has not less than two exits or exit-access doors, one of which is permitted to pass through the adjoining compartment, and

  - At least one exit or exit-access door from the day-care facility shall be into a separate means of egress with not less than two paths of exit travel, which are separated in such a manner to provide an atmospheric separation. The egress system shall comply with the requirements of Section 709 for smoke barriers.

  - The building is equipped with an automatic sprinkler system throughout.

452.1.5 Special Hazards

School classrooms constructed after January 1, 1990, not equipped with automatic sprinkler systems, which have metal grilles or bars on all their windows and do not have at least two exit doors within 3 feet (914 mm) of each end of the classroom opening to the exterior of the building or to a common hallway used for evacuation purposes, shall have an inside release for the grilles or bars on at least one window farthest from the exit doors. The window or windows with the inside release shall be clearly marked as emergency exits.

452.1.6

Class I, II or III-A flammable liquids shall not be placed, stored or used in Group E occupancies, except in approved quantities as necessary in laboratories and classrooms and for operation and maintenance as set forth in the California Fire Code.

Section 453 Group L [SFM]

453.1 Scope

The provisions of this section shall apply to buildings or structures, or portions thereof, containing one or more Group L laboratory suites as defined in Section 202.

The provisions of this section are optional and may apply to buildings or structures. See Section 304 for Group B Laboratories.

453.1.1 Technical Report

The enforcing agency may require a technical opinion and report to identify and develop methods of protection from the hazards presented by the hazardous materials. A qualified person, firm or corporation, approved by the enforcing agency, shall prepare the opinion and report, and shall be provided without charge to the enforcing agency. The opinion and report may include, but is not limited to, the preparation of a hazardous material management plan (HMMP); chemical analysis; recommendations for methods of isolation, separation, containment or protection of hazardous materials or processes, including appropriate engineering controls to be applied; the extent of changes in the hazardous behavior to be anticipated under conditions of exposure to fire or from hazard control procedures; and the limitations or conditions of use necessary to achieve and maintain control of the hazardous materials or operations. The report shall be entered into the files of the code enforcement agencies. Proprietary and trade secret information shall be protected under the laws of the state or jurisdiction having authority.

453.2 Definitions

The following terms are defined in Chapter 2:

Laboratory Suite

[F] Liquid Tight Floor

453.3 Laboratory Suite Requirements

453.3.1

Diagram

The gross floor area of an individual laboratory suite shall not exceed 10,000 square feet (929 m2).

UpCodes Diagrams (2)

Gross vs. Net Area

Gross Area Calc.

453.3.2

An individual laboratory suite shall not serve more than a single tenant.

Exception: An individual laboratory suite shall have a responsible party or department for all hazardous materials within a suite.

453.4 Construction

453.4.1 Separation of Laboratory Suites

453.4.1.1

Laboratory suites shall be separated from other occupancies in accordance with Table 508.4.

453.4.1.2

Laboratory suites shall be separated from other laboratory suites by a fire barrier having a fire-resistance rating of not less than 1-hour.

453.4.1.3

Laboratory suites shall be separated from control areas by a minimum 2-hour fire-resistance rating in accordance with Sections 707 and 711.

Exception: Laboratory suites shall be separated from control areas by a minimum 1-hour fire-resistance rating on floor levels below the 4th story.

453.4.1.4 Horizontal Separation

The floor construction of the laboratory suite and the construction supporting the floor of the laboratory suite shall have a minimum 2-hour fire-resistance rating in accordance with Section 711.

Exceptions:

- The floor construction of the laboratory suite and the construction supporting the floor of the laboratory suite are allowed to be 1-hour fire-resistance rated in buildings of Type IIA, IIIA and VA construction.

- When an individual laboratory suite occupies more than one story, the intermediate floors contained within the suite shall comply with the requirements of Table 601.

453.4.2

Reserved.

453.4.3 Fire Barrier and Fire-Smoke Barrier

453.4.3.1 Fire Barrier

A fire barrier having a fire resistance rating of not less than 2-hours shall divide any story containing more than one laboratory suite on the 4th story and above.

453.4.3.1.1

Fire barriers shall be continuous from exterior wall to exterior wall,

453.4.3.1.2

The fire barrier shall divide the floor so that the square footage on each side of the 2-hour fire barrier is not less than 30 percent of the total floor area, and

453.4.3.1.3

The number of laboratory suites on each side of the 2-hour fire barrier shall not be less than 25 percent of the total number of laboratory suites on the floor.

453.4.3.2 Fire-Smoke Barrier

Any story containing a Group L occupancy on the 11th story and above shall be subdivided by a fire-smoke barrier constructed as a fire barrier having a fire-resistance rating of not less than 2 hours and shall also comply with the smoke barrier requirements of Section 709.

The 2-hour fire-smoke barrier shall be in accordance with Sections 453.4.3 through 453.4.3.2.3.

453.4.3.2.1

A minimum of one door opening shall be provided in the 2-hour fire-smoke barrier for emergency access.

453.4.3.2.2

Each side of the 2-hour fire-smoke barrier shall be designed as a separate smoke zone designed in accordance with Section 909.6.

453.4.3.2.3

The area on each side of the 2-hour fire- smoke barrier shall be served by a minimum of one exit enclosure in accordance with Section 1022.

453.4.4 Emergency Response Equipment Area

When required by the fire code official, an area for emergency response equipment shall be provided on each floor in an approved location. The area shall be a minimum of 50 square feet (4.6 m2), for spill mitigation supplies per California Fire Code 5001.3.3.4 in a location approved by the fire code official, and identified with signage.

Exception: The area size for spill mitigation supplies may be reduced by the fire code official when adequate supplies are provided.

453.4.5 Liquid Tight Floor

All portions of the laboratory suite where hazardous materials may be stored, dispensed, handled or used shall be provided with a liquid tight floor. The intersections of such floors shall have an integral coved base that extends upward onto the wall not less than 2 inches. Where the floor is designed to provide spill control or secondary containment the floor shall be designed in accordance with California Fire Code Section 5004.2.

453.4.6 Secondary Power Systems

A legally required standby power system shall have an automatic transfer time of not more than 10 seconds.

453.4.6.1 Required Systems

Standby power shall be provided for all electrically operated equipment, systems and connected control circuits including:

- Mechanical ventilation systems. See Section 453.4.7.2.

- Temperature control systems required to prevent unsafe process excursions or chemical reactions.

- Treatment systems and scrubbers.

- Emergency Responder Radio Coverage (ERRCS). See Section 510 of the California Fire Code.

- Electrically operated systems required elsewhere in this code and the California Fire Code.

453.4.7 Ventilation

453.4.7.1 Compatibility

Incompatible materials shall not be conveyed in the same duct system. Combined products in mechanical exhaust ducts shall not create a physical hazard or reaction that could degrade the duct material. The building official may require a technical report in accordance with Section 453.7.1.

453.4.7.2 Fire Dampers, Smoke Dampers and Combination Fire/Smoke Dampers

Fire dampers, smoke dampers or fire/smoke dampers shall not be permitted in mechanical exhaust duct systems used to maintain a safe laboratory environment. When the exhaust duct penetrates the laboratory suite boundary the exhaust duct shall be located within a horizontal or vertical assembly having a fire resistance rating equal to the fire barrier.

453.4.7.3

Reserved.

453.4.7.4 Laboratory Suite Exhaust Air

453.4.7.4.1

Exhaust air from laboratory suites shall not be recirculated.

453.4.7.4.2

Laboratory suite exhaust air shall be independently ducted to a point outside the building or an approved roof top structure.

Exception: Exhaust ducts serving separate laboratory suites may be connected to a common duct within a fire rated vertical shaft when the sub-duct extends vertically upward at least 22 inches.

453.4.7.4.3

Laboratory suite exhaust ducts shall not penetrate the fire barriers required by Section 453.4.1.

Exception: Where the exhaust duct is enclosed in a rated shaft in accordance with Section 713.

453.4.7.5 Ventilation Rates

Mechanical exhaust ventilation systems shall provide a minimum ventilation rate not less than 1 cubic feet per minute per square foot [0.00508 m3/(s•m2)] of floor area, or 6 air exchanges per hour, whichever is greater. Systems shall operate continuously at the designed ventilation rate.

Exception: Refer to California Fire Code Section 5001.3 Performance-based design alternatives, as approved by the Fire Code Official.

453.4.7.6

Reserved.

453.4.7.7 Mechanical Ventilation System Balancing

Mechanical ventilation systems shall be designed and balanced such that during normal and emergency conditions the door opening forces comply with the requirements of Sections 1010.1.3 and Chapter 11B as applicable. Emergency conditions shall include: supply fan shutdown or failure, closing of smoke dampers or combination fire/smoke dampers, or emergency power.

453.5 Fire Protection Systems

See Chapter 9.

453.6 Means of Egress

453.6.1 Access to Exits

Every room of a laboratory suite containing hazardous materials and having a floor area of 500 square feet (19 m2) or more shall have access to not less than two separate exits or exit-access doorways in accordance with Section 1006.2.

453.6.2 Door Swing

All exit and exit-access doors serving areas with hazardous materials shall swing in the direction of exit travel, regardless of the occupant load served.

453.6.3 Panic Hardware

Exit and exit access doors from areas with hazardous materials shall not be provided with a latch or lock unless it is panic hardware or fire exit hardware.

453.6.4 Buildings of Four Stories or More

A minimum of one exit shall be provided to serve the floor on each side of the 2-hour fire barrier and shall comply with the provisions of Chapter 10.

453.6.5

Reserved.

453.7 Hazardous Materials

453.7.1 Multiple Hazards

When a hazardous material has multiple hazards, all hazards shall be addressed and controlled in accordance with the provisions of this code and the California Fire Code.

453.7.2 Percentage of Maximum Allowable Quantities

The percentage of the maximum allowable quantity of hazardous materials per laboratory suite permitted for each story level within a building shall be in accordance with Table 453.7.2.1.

TABLE 453.7.2.1— HAZARDOUS MATERIALS QUANTITY PER LABORATORY SUITE

| STORY |  | PERCENTAGE OF MAXIMUM ALLOWABLE QUANTITY PER LABORATORY SUITEa, b | NUMBER OF LAB SUITES PER FLOOR BASED ON CONSTRUCTION TYPE |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Type IA | Type IB | Type IIA, IIIA, IV | Type IIB, IIIB, VA | Type VB |
| Above grade plane | Above 20 | 0 | NP | NP | NP | NP | NP |
|  | 15 to 20 | 25 | 4 | NP | NP | NP | NP |
|  | 11, 12, 13, 14 | 50 | 8 | NP | NP | NP | NP |
|  | 7, 8, 9, 10 | 50 | 16 | NP | NP | NP | NP |
|  | 6 | 75 | 20 | 20 | NP | NP | NP |
|  | 4, 5 | 75 | 20 | 20 | 20 | NP | NP |
|  | 3 | 100 | UL | UL | UL | UL | NP |
|  | 1, 2 | 100 | UL | UL | UL | UL | UL |
| Below grade plane | 1 | 75c | 10 | 10 | 10 | 10 | 10 |
|  | 2 | 50d | 5 | 5 | 5 | 5 | 5 |
|  | 3 and below | 0 | NP | NP | NP | NP | NP |

UL = Unlimited, NP = Not permitted

- Percentages shall be of the maximum allowable quantity per laboratory suite shown in Tables 307.1(1) and 307.1(2). Allowable hazardous material increases for buildings equipped throughout with an automatic sprinkler system shall not be applicable to Group L occupancies.

- When an individual laboratory suite occupies more than one story, the more restrictive percentage of the maximum allowable quantity per laboratory suite shall apply.

- The total aggregate quantity of flammable liquids on the first story below grade shall be limited to the maximum total aggregate quantity for Group B occupancy control areas.

- The total aggregate quantity of flammable liquids on the second story level below grade shall be limited to a maximum total aggregate quantity for Group B occupancy control areas.

453.7.3 Handling and Transportation

The handling and transportation of hazardous materials shall be in accordance with Section 5003.10 of the California Fire Code.

453.8 Elevators and Elevator Lobbies on the 11th Story and Above

Any story containing a Group L occupancy on the 11th story and above shall be provided with elevators and elevator lobbies in accordance with Sections 453.8.1 through 453.8.3.

453.8.1

An elevator that serves every story of the building shall be provided on each side of the 2-hour fire-smoke barrier.

453.8.2

An elevator lobby shall be provided on each side of the 2-hour fire-smoke barrier at each floor in accordance with Section 3006.

453.8.3

The elevator and its associated elevator lobbies and elevator machine rooms shall be pressurized in accordance with Section 909.6.

453.9 Existing Group L and Group H-8 Occupancies, Additions, Alterations or Repairs

See California Fire Code Chapter 11, Section 1116 and California Existing Building Code.

Section 454 Reserved

Section 455 Large Family Day-Care Homes [SFM]

455.1 Large Family Day-Care Homes

455.2

For purposes of clarification, Health and Safety Code Sections 1597.45 and 1597.46 are repeated.

1597.45.

- The use of a home as a small or large family day-care home shall be considered a residential use of property and a use by right for the purposes of all local ordinances, including, but not limited to, zoning ordinances.

- A local jurisdiction shall not impose a business license, fee or tax for the privilege of operating a small or large family day-care home.

- Use of a home as a small or large family day-care home shall not constitute a change of occupancy for purposes of Part 1.5 (commencing with Section 17910) of Division 13 (State Housing Law) or for purposes of local building codes.

- A small or large family day-care home shall not be subject to the provisions of Division 13 (commencing with Section 21000) of the Public Resources Code.

- The provisions of this chapter do not preclude a city, county or other local public entity from placing restrictions on building heights, setback or lot dimensions of a family day-care home, as long as those restrictions are identical to those applied to all other residences with the same zoning designation as the family day-care home. This chapter does not preclude a local ordinance that deals with health and safety, building standards, environmental impact standards or any other matter within the jurisdiction of a local public entity, as long as the local ordinance is identical to those applied to all other residences with the same zoning designation as the family day-care home. This chapter also does not prohibit or restrict the abatement of nuisances by a city, county, or city and county. However, the ordinance or nuisance abatement shall not distinguish family day-care homes from other homes with the same zoning designation, except as otherwise provided in this chapter.

- For purposes of this chapter, "small family day-care home or large family day-care home" includes a detached single-family dwelling, a townhouse, a dwelling unit within a dwelling or a dwelling unit within a covered multifamily dwelling in which the underlying zoning allows for residential uses. A small family day-care home or large family day-care home is where the family day-care provider resides and includes a dwelling or dwelling unit that is rented, leased or owned.

(Amended by Stats. 2019, Ch. 244, Sec. 9. (SB 234) Effective January 1, 2020.)

1597.46.

- A large family day-care home shall abide by all standards, in addition to the requirements of the State Uniform Building Standards Code, that are specifically designed to promote fire and life safety in large family day-care homes. The State Fire Marshal shall adopt separate building standards specifically relating to the subject of fire and life safety in family day-care homes, which shall be published in Title 24 of the California Code of Regulations. These standards shall apply uniformly throughout the state and shall include, but not be limited to, all of the following:

  - The requirement that a large family day-care home contain a fire extinguisher or smoke detector device, or both, that meets child-care standards established by the State Fire Marshal.

  - Specification as to the number of required exits from the home.

  - Specification as to the floor or floors on which child care may be provided and the number of required exits on each floor.

- A large family day-care home for children shall have one or more carbon monoxide detectors in the facility that meet the standards established in Chapter 8 (commencing with Section 13260) of Part 2 of Division 12. The department shall account for the presence of these detectors during inspections.

- Enforcement of this section shall be in accordance with Sections 13145 and 13146. A city, county, city and county, or district shall not adopt or enforce a building ordinance or local rule or regulation relating to the subject of fire and life safety in large family day-care homes that is inconsistent with those standards adopted by the State Fire Marshal, except to the extent the building ordinance or local rule or regulation applies to all residences with the same zoning designation in which child care is provided.

(Repealed and added by Stats. 2019, Ch. 244, Sec. 12. (SB 234) Effective January 1, 2020.)

455.3 Smoke Alarms

Large family day-care homes shall be equipped with State Fire Marshal approved and listed single station residential type smoke alarms. The number and placement of smoke alarms shall be determined by the enforcement authority.

455.4 Fire Extinguishers

Large and small family day-care homes shall be equipped with a portable fire extinguisher having a minimum 2A10BC rating.

455.5 Fire Alarm Devices

See Section 907.2.6.4.

455.6 Compliance

Every large-family day-care home shall comply with the provisions for Group R-3 occupancies. For the purposes of Section 436.1, the first story shall be designated as the floor used for residential occupancy nearest to the street level which provides primary access to the building.

455.7 Special Hazards

Every unenclosed gas-fired water heater or furnace which is within the area used for child care in a large family day-care home shall be protected in such a way as to prevent children from making contact with those appliances.

Exception: This does not apply to kitchen stoves or ovens.

455.8 Exiting

See Section 1006.2.2.7.