Chapter 31 Special Construction

CALIFORNIA BUILDING CODE — MATRIX ADOPTION TABLE CHAPTER 31 — SPECIAL CONSTRUCTION

(Matrix Adoption Tables are nonregulatory, intended only as an aid to the code user.
See Chapter 1 for state agency authority and building applications.)

| Adopting agency | BSC | BSC- CG | SFM | HCD |  |  | DSA |  |  | OSHPD |  |  |  |  |  |  | BSCC | DPH | AGR | DWR | CEC | CA | SL | SLC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 1/AC | AC | SS | SS/CC | 1 | 1R | 2 | 3 | 4 | 5 | 6 |  |  |  |  |  |  |  |  |
| Adopt entire chapter |  |  |  |  |  |  |  |  |  | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |
| Adopt entire chapter as amended (amended sections listed below) |  |  |  | X | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Adopt only those sections that are listed below | X |  | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapter / Section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3101 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3102 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3103 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3103.1 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3104 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3104.2, Exception 2 |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3105 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3106 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3109 |  |  |  | † | † |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3109.1 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3109.2, Note | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3110 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3111 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3111.1.1, Exception |  |  |  | X | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3112.2 |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3112.3, Exception |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113 |  |  |  | † | † |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113.1 |  |  |  | X | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113.1.1 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113.2, Exception |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113.3, Exception |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3113.4, Exception |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3114 |  |  | X |  |  |  |  |  |  | † | † | † |  | † | † |  |  |  |  |  |  |  |  |  |
| 3114.1, Exceptions |  |  |  | X | X |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3114.6, Exception |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3114.8.4.2 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3114.8.5 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3114.9 |  |  |  |  |  |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

The state agency does not adopt sections identified with the following symbol: †

The Office of the State Fire Marshal's adoption of this chapter or individual sections is applicable to structures regulated by other state agencies pursuant to Section 1.11.

User notes:

About this chapter: Chapter 31 provides regulations for unique buildings and building elements. Those include buildings such as membrane structures, greenhouses and relocatable buildings. Special elements include pedestrian walkways and tunnels, awnings, canopies and marquees, vehicular gates, solar energy systems, public use restrooms in flood hazard areas, and intermodal shipping containers.

ICC code development note: Code development reminder: Code change proposals to sections preceded by the designation [F] and [BE] will be considered by a code development committee meeting during the 2024 (Group A) Code Development Cycle. All other code change proposals will be considered by a code development committee meeting during the 2025 (Group B) Code Development Cycle.

Section 3101 General

3101.1 Scope

The provisions of this chapter shall govern special building construction including membrane structures, temporary structures, pedestrian walkways and tunnels, awnings and canopies, marquees, signs, telecommunications and broadcast towers, swimming pools, spas and hot tubs, automatic vehicular gates, solar energy systems, greenhouses, relocatable buildings and intermodal shipping containers.

[OSHPD 1, 1R, 2, 4 & 5] The provisions of this chapter shall govern special building construction, including membrane structures, temporary structures, pedestrian walkways and tunnels, automatic vehicular gates, awnings and canopies, marquees, signs, towers, antennas, relocatable buildings, swimming pool enclosures and safety devices, solar energy systems, public use restroom buildings on publicly owned lands in flood hazard areas and intermodal shipping containers.

[OSHPD 1, 1R, 2, 4 & 5]

The provisions of this chapter shall govern special building construction, including membrane structures, temporary structures, pedestrian walkways and tunnels, automatic vehicular gates, awnings and canopies, marquees, signs, towers, antennas, relocatable buildings, swimming pool enclosures and safety devices, solar energy systems, public use restroom buildings on publicly owned lands in flood hazard areas and intermodal shipping containers.

Section 3102 Membrane Structures

3102.1 General

The provisions of Sections 3102.1 through 3102.8 shall apply to air-supported, air-inflated, membrane-covered cable, membrane-covered frame and tensile membrane structures, collectively known as membrane structures, erected for a period of 180 days or longer. Those erected for a shorter period of time shall comply with the California Fire Code. Membrane structures covering water storage facilities, water clarifiers, water treatment plants, sewage treatment plants, greenhouses and similar facilities not used for human occupancy are required to meet only the requirements of Sections 3102.3.1 and 3102.7. Membrane structures erected on a building, balcony, deck or other structure for any period of time shall comply with this section.

3102.2 Tensile Membrane Structures and Air-Supported Structures

Tensile membrane structures and air-supported structures, including permanent and temporary structures, shall be designed and constructed in accordance with ASCE 55. The provisions in Sections 3102.3 through 3102.6 shall apply.

3102.3 Type of Construction

Noncombustible membrane structures shall be classified as Type IIB construction. Noncombustible frame or cable-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IIB construction. Heavy timber frame-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IV-HT construction. Other membrane structures shall be classified as Type V construction.

Exception: Plastic less than 30 feet (9144 mm) above any floor used in greenhouses, where occupancy by the general public is not authorized, and for aquaculture pond covers is not required to meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

3102.3.1 Membrane and Interior Liner Material

Membranes and interior liners shall be either noncombustible as set forth in Section 703.3 shall be flame resistant in accordance with the provisions set forth in CCR, Title 19, Division 1, Chapter 8. Tops and sidewalls shall be made either from fabric that has been flame resistant treated with an approved exterior chemical process by an approved application concern, or from inherently flame resistant fabric approved and listed by the State Fire Marshal (see CCR, Title 19, Division 1, Chapter 8).

Exception: Plastic less than 20 mil (0.5 mm) in thickness used in greenhouses, where occupancy by the general public is not authorized, and for aquaculture pond covers is not required to meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

3102.4 Allowable Floor Areas

The area of a membrane structure shall not exceed the limitations specified in Section 506.

3102.5 Maximum Height

Membrane structures shall not exceed one story nor shall such structures exceed the height limitations in feet specified in Section 504.3.

Exception: Noncombustible membrane structures serving as roofs only.

3102.6 Mixed Construction

Membrane structures shall be permitted to be utilized as specified in this section as a portion of buildings of other types of construction. Height and area limits shall be as specified for the type of construction and occupancy of the building.

3102.6.1 Noncombustible Membrane

A noncombustible membrane shall be permitted for use as the roof or as a skylight of any building or atrium of a building of any type of construction provided that the membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery.

3102.6.1.1 Membrane

A membrane meeting the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be permitted to be used as the roof or as a skylight on buildings of Type IIB, III, IV-HT and V construction, provided that the membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery.

3102.7 Engineering Design

The structure shall be designed and constructed to sustain dead loads; loads due to tension or inflation; live loads including wind, snow or flood and seismic loads and in accordance with Chapter 16.

3102.7.1 Lateral Restraint

For membrane-covered frame structures, the membrane shall not be considered to provide lateral restraint in the calculation of the capacities of the frame members.

3102.8 Inflation Systems

Air-supported and air-inflated structures shall be provided with primary and auxiliary inflation systems to meet the minimum requirements of Sections 3102.8.1 through 3102.8.3.

3102.8.1 Equipment Requirements

The inflation system shall consist of one or more blowers and shall include provisions for automatic control to maintain the required inflation pressures. The system shall be so designed as to prevent overpressurization of the system.

3102.8.1.1 Auxiliary Inflation System

In addition to the primary inflation system, in buildings larger than 1,500 square feet (140 m2) in area, an auxiliary inflation system shall be provided with sufficient capacity to maintain the inflation of the structure in case of primary system failure. The auxiliary inflation system shall operate automatically when there is a loss of internal pressure and when the primary blower system becomes inoperative.

3102.8.1.2 Blower Equipment

Blower equipment shall meet all of the following requirements:

- Blowers shall be powered by continuous-rated motors at the maximum power required for any flow condition as required by the structural design.

- Blowers shall be provided with inlet screens, belt guards and other protective devices as required by the building official to provide protection from injury.

- Blowers shall be housed within a weather-protecting structure.

- Blowers shall be equipped with backdraft check dampers to minimize air loss when inoperative.

- Blower inlets shall be located to provide protection from air contamination. The location of inlets shall be approved.

3102.8.2 Standby Power

Diagram

Wherever an auxiliary inflation system is required, an approved standby power-generating system shall be provided. The system shall be equipped with a suitable means for automatically starting the generator set upon failure of the normal electrical service and for automatic transfer and operation of all of the required electrical functions at full power within 60 seconds of such service failure. Standby power shall be capable of operating independently for not less than 4 hours.

UpCodes Diagram (1)

Standby Power Systems

3102.8.3 Support Provisions

A system capable of supporting the membrane in the event of deflation shall be provided for in air-supported and air-inflated structures having an occupant load of 50 or more or where covering a swimming pool regardless of occupant load. The support system shall be capable of maintaining membrane structures used as a roof for Type I construction not less than 20 feet (6096 mm) above floor or seating areas. The support system shall be capable of maintaining other membranes not less than 7 feet (2134 mm) above the floor, seating area or surface of the water.

Section 3103 Temporary Structures

Diagram

UpCodes Diagram (1)

Egress Req. for Temporary Structures

3103.1 General

The provisions of Sections 3103.1 through 3103.8 shall apply to structures erected for a period of less than 180 days. Temporary special event structures, tents, umbrella structures and other membrane structures erected for a period of less than 180 days shall also comply with the California Fire Code. Temporary structures erected for a longer period of time and public-occupancy temporary structures shall comply with applicable sections of this code.

Exceptions:

- Public-occupancy temporary structures complying with Section 3103.1.1 shall be permitted to remain in service for 180 days or more but not more than 1 year where approved by the building official.

- Public-occupancy temporary structures within the confines of an existing structure are not required to comply with Section 3103.6.

[DSA-SS, DSA-SS/CC] The classification of public-occupancy temporary structure shall not be applied to any school building as defined in Section 4-314 of the California Administrative Code.

[DSA-SS, DSA-SS/CC]

The classification of public-occupancy temporary structure shall not be applied to any school building as defined in Section 4-314 of the California Administrative Code.

3103.1.1 Extended Period of Service Time

Public-occupancy temporary structures shall be permitted to remain in service for 180 days or more without complying with requirements in this code for new building or structures where extensions for up to 1 year are granted by the Building Official in accordance with Section 108.1 and where the following conditions are satisfied:

- Additional inspections as determined by the building official shall be performed by a qualified person to verify that site conditions and the approved installation comply with the conditions of approval at the time of final inspection.

- A qualified person shall perform follow-up inspections after initial occupancy at intervals not exceeding 180 days to verify the site conditions and the installation conform to the approved site conditions and installation requirements. Inspection records shall be kept and shall be made available for verification by the building official.

- An examination shall be performed by a registered design professional to determine the adequacy of the temporary structure to resist the structural loads required in Section 3103.6.

- Relocation of the public-occupancy temporary structure shall require a new permit application.

- The use or occupancy approved at the time of final inspection shall remain unchanged.

- A request for an extension is submitted to the building official. The request shall include records of the inspections and examination in Items 1 and 3.

3103.1.2 Conformance

Temporary structures and uses shall conform to the structural strength, fire safety, means of egress, accessibility, light, ventilation and sanitary requirements of this code as necessary to ensure public health, safety and general welfare.

3103.1.2.1 Water-Filled Vessels

[SFM] Water-filled vessels shall not be used to anchor a tent or membrane structure unless approved and in accordance with the tent or membrane structure manufacturer's instructions.

3103.1.3 Permit Required

Temporary structures that cover an area greater than 120 square feet (11.16 m2), including connecting areas or spaces with a common means of egress or entrance that are used or intended to be used for the gathering together of 10 or more persons, shall not be erected, operated or maintained for any purpose without obtaining a permit from the building official.

3103.2 Construction Documents

A permit application and construction documents shall be submitted for each installation of a temporary structure. The construction documents, shall include a site plan indicating the location of the temporary structure and information delineating the means of egress and the occupant load.

3103.3 Location

Temporary structures shall be located in accordance with the requirements of Table 705.5 based on the fire-resistance rating of the exterior walls for the proposed type of construction.

3103.4 Means of Egress

Diagram

Temporary structures shall conform to the means of egress requirements of Chapter 10 and shall have an exit access travel distance of 100 feet (30 480 mm) or less.

UpCodes Diagram (1)

Primary

Egress Req. for Temporary Structures

3103.5 Bleachers

Temporary bleachers, grandstands and folding and telescopic seating that are not building elements shall comply with ICC 300.

3103.6 Structural Requirements

Temporary structures shall comply with the structural requirements of this code. Public-occupancy temporary structures shall be designed and erected to comply with the structural requirements of this code and Sections 3103.6.1 through 3103.6.4.

Exception: Where approved, live loads less than those prescribed by Table 1607.1 shall be permitted provided that a registered design professional demonstrates that a rational approach has been used and that such reductions are warranted.

Temporary non-building structures ancillary to public assemblies or special event structures whose structural failure or collapse would endanger assembled public shall be assigned a risk category corresponding to the risk category of the public assembly. For the purposes of establishing an occupant load for the assembled public endangered by structural failure or collapse, the applicable occupant load determination in Section 1004.5 or 1004.6 shall be applied over the assembly area within a radius equal to 1.5 times the height of the temporary non-building structure

3103.6.1 Structural Loads

Public-occupancy temporary structures shall be designed in accordance with Chapter 16, except as modified by Sections 3103.6.1.1 through 3103.6.1.6.

3103.6.1.1 Snow Loads

Snow loads on public-occupancy temporary structures shall be determined in accordance with Section 1608. The ground snow loads, pg, in Section 1608 shall be modified according to Table 3103.6.1.1.

Exception: Ground snow loads, pg, for public-occupancy temporary structures that employ controlled-occupancy procedures per Section 3103.8 shall be permitted to be modified using a ground snow load reduction factor of 0.65 instead of the ground snow load reduction factors in Table 3103.6.1.1.

Where the public-occupancy temporary structure is not subject to snow loads or not constructed and occupied during times when snow is to be expected, snow loads need not be considered, provided that where the period of time when the public-occupancy temporary structure is in service shifts to include times when snow is to be expected, one of the following conditions is met:

- The design is reviewed and modified, as appropriate, to account for snow loads.

- Controlled occupancy procedures in accordance with Section 3103.8 are implemented.

TABLE 3103.6.1.1—REDUCTION FACTORS FOR GROUND SNOW LOADS FOR PUBLIC-OCCUPANCY TEMPORARY STRUCTURES

| RISK CATEGORY | SERVICE LIFE |  |
| --- | --- | --- |
|  | ≤ 10 yr | >10 yr |
| II | 0.7 | 1.0 |
| III | 0.8 | 1.0 |
| IV | 1.0 | 1.0 |

3103.6.1.2 Wind Loads

The design wind load on public-occupancy temporary structures shall be permitted to be modified in accordance with the wind load reduction factors in Table 3103.6.1.2.

Exceptions:

- Design wind loads for public-occupancy temporary structures that implement controlled occupancy procedures per Section 3103.8 shall be permitted to be modified using a wind load reduction factor of 0.65.

- For public-occupancy temporary structures erected in a hurricane-prone region outside of hurricane season, the basic wind speed, V, shall be permitted to be set as follows, depending on risk category:

  - 2.1.  Risk Category II: 115 mph.

  - 2.2.  Risk Category III: 120 mph.

  - 2.3.  Risk Category IV: 125 mph.

TABLE 3103.6.1.2—REDUCTION FACTORS FOR WIND LOADS FOR PUBLIC-OCCUPANCY TEMPORARY STRUCTURES

| RISK CATEGORY | SERVICE LIFE |  |
| --- | --- | --- |
|  | ≤ 10 yr | >10 yr |
| II | 0.8 | 1.0 |
| III | 0.9 | 1.0 |
| IV | 1.0 | 1.0 |

3103.6.1.3 Flood Loads

Public-occupancy temporary structures need not be designed for flood loads specified in Section 1612. Controlled occupancy procedures in accordance with Section 3103.8 shall be implemented.

3103.6.1.4 Seismic Loads

Seismic loads on public-occupancy temporary structures assigned to Seismic Design Categories C through F shall be permitted to be taken as 75 percent of those determined by Section 1613. Public-occupancy temporary structures assigned to Seismic Design Categories A and B are not required to be designed for seismic loads.

3103.6.1.5 Ice Loads

Ice loads on public-occupancy temporary structures shall be permitted to be determined with a maximum nominal thickness of 0.5 inch (13 mm), for all risk categories. Where the public-occupancy temporary structure is not subject to ice loads or not constructed and occupied during times when ice is to be expected, ice loads need not be considered, provided that where the period of time when the public-occupancy temporary structure is in service shifts to include times when ice is to be expected, one of the following conditions is met:

- The design is reviewed and modified, as appropriate, to account for ice loads.

- Controlled occupancy procedures in accordance with Section 3103.8 are implemented.

3103.6.1.6 Tsunami Loads

Public-occupancy temporary structures in a tsunami design zone are not required to be designed for tsunami loads specified in Section 1615. Controlled occupancy procedures in accordance with Section 3103.8 shall be implemented.

3103.6.2 Foundations

Public-occupancy temporary structures shall be permitted to be supported on the ground with temporary foundations where approved by the building official. Consideration shall be given for the impacts of differential settlement where foundations do not extend below the ground or where foundations are supported on compressible materials. The presumptive load-bearing value for public-occupancy temporary structures supported on a pavement, slab on grade or on other collapsible or controlled low-strength substrate soils such as beach sand or grass shall be assumed not to exceed 1,000 pounds per square foot (47.88 kPa) unless determined through testing and evaluation by a registered design professional. The presumptive load-bearing values listed in Table 1806.2 shall be permitted to be used for other supporting soil conditions.

3103.6.3 Installation and Maintenance Inspections

A qualified person shall inspect public-occupancy temporary structures that are assembled using transportable and reusable materials. Components shall be inspected when purchased or acquired and at least once per year. The inspection shall evaluate individual components, and the fully assembled structure, to determine suitability for use based on the requirements in ESTA ANSI E1.21. Inspection records shall be kept and shall be made available for verification by the building official. Additionally, public-occupancy temporary structures shall be inspected at regular intervals when in service to ensure that the structure continues to perform as designed and initially erected.

3103.6.4 Durability

Reusable components used in the erection and the installation of public-occupancy temporary structures shall be manufactured of durable materials necessary to withstand environmental conditions at the service location. Components damaged during transportation or installation or due to the effects of weathering shall be replaced or repaired.

3103.7 Serviceability

The effects of structural loads or conditions shall not adversely affect the serviceability or performance of the public-occupancy temporary structure.

3103.8 Controlled Occupancy Procedures

Where controlled occupancy procedures are required to be implemented for public-occupancy temporary structures in Section 3103.6.1, the procedures shall comply with this section and ANSI ES1.7. An operations management plan in accordance with ANSI E1.21 shall be submitted to the building official for approval as a part of the permit documents. In addition, the operations management plan shall include an emergency action plan that documents the following information, where applicable:

- Surfaces on which snow or ice accumulates shall be monitored before and during occupancy of the public-occupancy temporary structure. Any loads in excess of the design snow or ice load shall be removed prior to its occupancy, or the public-occupancy temporary structure shall be vacated in the event that either the design snow or ice load is exceeded during its occupancy.

- Wind speeds associated with the design wind loads shall be monitored before and during occupancy of the public-occupancy temporary structure. The public-occupancy temporary structure shall be vacated in the event that the design windspeed is expected to be exceeded during its occupancy.

- Criteria for initiating occupant evacuation procedures for flood and tsunami events.

- Occupant evacuation procedures shall be specified for each environmental hazard where the occupant management plan specifies the public-occupancy temporary structure is to be evacuated.

- Procedures for anchoring or removal of the public-occupancy temporary structure, or other additional measures or procedures to be implemented to mitigate hazards in snow, wind, flood, ice or tsunami events.

Section 3104 Pedestrian Walkways and Tunnels

3104.1 General

This section shall apply to connections between buildings such as pedestrian walkways or tunnels, located at, above or below grade level, that are used as a means of travel by persons. The pedestrian walkway shall not contribute to the building area or the number of stories or height of connected buildings.

3104.1.1 Application

Pedestrian walkways shall be designed and constructed in accordance with Sections 3104.2 through 3104.9. Tunnels shall be designed and constructed in accordance with Sections 3104.2 and 3104.10.

3104.2 Separate Structures

Buildings connected by pedestrian walkways or tunnels shall be considered to be separate structures.

Exceptions:

- Buildings that are on the same lot and considered as portions of a single building in accordance with Section 503.1.2.

- [DSA-AC and HCD 1-AC] For purposes of accessibility in residential facilities as required by Chapters 11A and 11B, structurally connected buildings, buildings connected by stairs, walkways or roofs, and buildings with multiple wings shall be considered one structure.

3104.3 Construction

The pedestrian walkway shall be of noncombustible construction.

Exceptions:

- Combustible construction shall be permitted where connected buildings are of combustible construction.

- Fire-retardant-treated wood, in accordance with Section 603.1, Item 1.3, shall be permitted for the roof construction of the pedestrian walkway where connected buildings are not less than Type I or II construction.

Building products (3)

Back Up Pavers 4 x 2¼ x 7⅝

Interstate Brick

Modular Paver 4 x 2¼ x 7⅝

Interstate Brick

True Paver 4 x 2¼ x 8

Interstate Brick

3104.4 Contents

Only materials and decorations approved by the building official shall be located in the pedestrian walkway.

3104.5 Connections of Pedestrian Walkways to Buildings

The connection of a pedestrian walkway to a building shall comply with Section 3104.5.1, 3104.5.2, 3104.5.3 or 3104.5.4.

Exception: Buildings that are on the same lot and considered as portions of a single building in accordance with Section 503.1.2.

3104.5.1 Fire Barriers

Assembly

Pedestrian walkways shall be separated from the interior of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 and Sections 3104.5.1.1 through 3104.5.1.3.

Assemblies (19)

12-1.2: 2hr, Wood

11-1.2: 2hr, Steel Stud/ Plaster

15-1.9: 2hr, Steel Stud

6-1.2: 1hr & 2hr, Solid Gyp Plaster

6-2.2: 1hr & 2hr, Solid Gyp

7-1.1: 2hr, Steel Wire

8-1.1: 2hr, Steel

15-1.8: 2hr, Wood

15-1.7: 2hr, Wood

15-1.5: 2hr, Wood

Show 9 more

3104.5.1.1 Exterior Walls

Exterior walls of buildings connected to pedestrian walkways shall be 2-hour fire-resistance rated. This protection shall extend not less than 10 feet (3048 mm) in every direction surrounding the perimeter of the pedestrian walkway.

3104.5.1.2 Openings in Exterior Walls of Connected Buildings

Openings in exterior walls required to be fire-resistance rated in accordance with Section 3104.5.1.1 shall be equipped with opening protectives providing a not less than 3/4-hour fire protection rating in accordance with Section 716.

3104.5.1.3 Supporting Construction

The fire barrier shall be supported by construction as required by Section 707.5.1.

3104.5.2 Alternative Separation

The wall separating the pedestrian walkway and the building shall comply with Section 3104.5.2.1 or 3104.5.2.2 where:

- The distance between the connected buildings is more than 10 feet (3048 mm).

- The pedestrian walkway and connected buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and the roof of the walkway is not more than 55 feet (16 764 mm) above grade connecting to the fifth, or lower, story above grade plane, of each building.

Exception: Open parking garages need not be equipped with an automatic sprinkler system.

3104.5.2.1 Passage of Smoke

The wall shall be capable of resisting the passage of smoke.

3104.5.2.2 Glass

The wall shall be constructed of a tempered, wired or laminated glass and doors separating the interior of the building from the pedestrian walkway. The glass shall be protected by an automatic sprinkler system in accordance with Section 903.3.1.1 that, when actuated, shall completely wet the entire surface of interior sides of the wall or glass. Obstructions shall not be installed between the sprinkler heads and the wall or glass. The glass shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler operates.

3104.5.3 Open Sides on Walkway

Where the distance between the connected buildings is more than 10 feet (3048 mm), the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance rated provided that both sidewalls of the pedestrian walkway are not less than 50 percent open with the open area uniformly distributed to prevent the accumulation of smoke and toxic gases. The roof of the walkway shall be located not more than 40 feet (12 160 mm) above grade plane, and the walkway shall only be permitted to connect to the third or lower story of each building.

Exception: Where the pedestrian walkway is protected with an automatic sprinkler system in accordance with Section 903.3.1.1, the roof of the walkway shall be located not more than 55 feet (16 764 mm) above grade plane and the walkway shall only be permitted to connect to the fifth or lower story of each building.

3104.5.4 Exterior Walls Greater Than 2 Hours

Diagram

Where exterior walls of connected buildings are required by Section 705 to have a fire-resistance rating greater than 2 hours, the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance rated provided:

- The pedestrian walkway is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

- The roof of the walkway is not located more than 55 feet (16 764 mm) above grade plane and the walkway connects to the fifth, or lower, story above grade plane of each building.

UpCodes Diagram (1)

Grade Plane

3104.6 Public Way

Pedestrian walkways over a public way shall comply with Chapter 32.

[BE] 3104.7 Egress

Access shall be provided at all times to a pedestrian walkway that serves as a required exit.

[BE] 3104.8 Width

The unobstructed width of pedestrian walkways shall be not less than 36 inches (914 mm). The total width shall be not greater than 30 feet (9144 mm).

[BE] 3104.9 Exit Access Travel

The length of exit access travel shall be 200 feet (60 960 mm) or less.

Exceptions:

- Exit access travel distance on a pedestrian walkway equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be 250 feet (76 200 mm) or less.

- Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open shall be 300 feet (91 440 mm) or less.

- Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open, and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, shall be 400 feet (122 m) or less.

3104.10 Tunneled Walkway

Separation between the tunneled walkway and the building to which it is connected shall be not less than 2-hour fire-resistant construction and openings therein shall be protected in accordance with Section 716.

Section 3105 Awnings and Canopies

Diagram

UpCodes Diagrams (4)

Encroachments of Public Way at Steps and Awnings

Fire Walls at Horizontal Projections

Fire Walls at Horizontal Projections (Excpt. 1)

Fire Walls at Horizontal Projections (Excpt. 2)

3105.1 General

Awnings and canopies shall comply with the requirements of Sections 3105.2 and 3105.3 and other applicable sections of this code.

3105.2 Design and Construction

Awnings and canopies shall be designed and constructed to withstand wind or other lateral loads and live loads as required by Chapter 16 with due allowance for shape, open construction and similar features that relieve the pressures or loads. Structural members shall be protected to prevent deterioration. Awnings shall have frames of noncombustible material, fire-retardant-treated wood, heavy timber complying with Section 2304.11 or 1-hour construction, and shall be fixed, retractable, folding or collapsible.

3105.3 Awnings and Canopy Materials

Awnings and canopies shall be provided with an approved covering that complies with one of the following:

- The fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

- Has a flame spread index not greater than 25 when tested in accordance with ASTM E84 or UL 723.

- Meets all of the following criteria when tested in accordance with NFPA 286:

  - During the 40 kW exposure, flames shall not spread to the ceiling.

  - Flashover, as defined in NFPA 286, shall not occur.

  - The flame shall not spread to the outer extremity of the sample on any wall or ceiling.

  - The peak heat release rate throughout the test shall not exceed 800 kW.

All fabrics and all interior decorative fabrics or materials shall be flame resistant in accordance with the provisions set forth in CCR, Title 19, Division 1, Chapter 8. Tops and sidewalls shall be made either from fabric that has been flame resistant treated with an approved exterior chemical process by an approved application concern, or from inherently flame resistant fabric approved and listed by the State Fire Marshal (see CCR, Title 19, Division 1, Chapter 8).

Exception: The fire propagation performance and flame spread index requirements shall not apply to awnings installed on detached one- and two-family dwellings.

Section 3106 Marquees

Diagram

UpCodes Diagrams (3)

Fire Walls at Horizontal Projections

Fire Walls at Horizontal Projections (Excpt. 1)

Fire Walls at Horizontal Projections (Excpt. 2)

3106.1 General

Marquees shall comply with Sections 3106.2 through 3106.5 and other applicable sections of this code.

3106.2 Thickness

The height or thickness of a marquee measured vertically from its lowest to its highest point shall be not greater than 3 feet (914 mm) where the marquee projects more than two-thirds of the distance from the lot line to the curb line, and shall be not greater than 9 feet (2743 mm) where the marquee is less than two-thirds of the distance from the lot line to the curb line.

3106.3 Roof Construction

Where the roof or any part thereof is a skylight, the skylight shall comply with the requirements of Chapter 24. Every roof and skylight of a marquee shall be sloped to downspouts that shall conduct any drainage from the marquee in such a manner so as not to spill over the sidewalk.

3106.4 Location Prohibited

Every marquee shall be so located as not to interfere with the operation of any exterior standpipe, and such that the marquee does not obstruct the clear passage of stairways or exit discharge from the building or the installation or maintenance of street lighting.

3106.5 Construction

A marquee shall be supported entirely from the building and constructed of noncombustible materials. Marquees shall be designed as required in Chapter 16. Structural members shall be protected to prevent deterioration.

Section 3107 Signs

3107.1 General

Signs shall be designed, constructed and maintained in accordance with this code.

Section 3108 Telecommunication and Broadcast Towers

[BS] 3108.1 General

Towers shall be designed and constructed in accordance with the provisions of TIA 222. Towers shall be designed for seismic loads; exceptions related to seismic design listed in Section 2.7.3 of TIA 222 shall not apply. In Section 2.6.6.2 of TIA 222, the horizontal extent of Topographic Category 2, escarpments, shall be 16 times the height of the escarpment.

Exception: Single free-standing poles used to support antennas not greater than 75 feet (22 860 mm), measured from the top of the pole to grade, shall not be required to be noncombustible.

[BS] 3108.2 Location and Access

Towers shall be located such that guy wires and other accessories shall not cross or encroach on any street or other public space, or over above-ground electric utility lines, or encroach on any privately owned property without the written consent of the owner of the encroached-upon property, space or above-ground electric utility lines. Towers shall be equipped with climbing and working facilities in compliance with TIA 222. Access to the tower sites shall be limited as required by applicable OSHA, FCC and EPA regulations.

Section 3109 Swimming Pools, Spas and Hot Tubs

Diagram

UpCodes Diagrams (2)

Swimming Pool: Equipotential Bonding (NFPA 70)

Swimming Pools Next to Descending Slopes

3109.1 General

The design and construction of swimming pools, spas and hot tubs shall comply with this code. [DSA-SS and DSA-SS/CC] Swimming pools utilized for public school purposes shall also be designed, constructed and inspected in accordance with this code.

Building products (5)

Back Up Pavers 4 x 2¼ x 7⅝

Interstate Brick

Modular Paver 4 x 2¼ x 7⅝

Interstate Brick

Pool Coping 4 x 2¼ x 12

Interstate Brick

Pool Coping 4 x 2¼ x 9

Interstate Brick

True Paver 4 x 2¼ x 8

Interstate Brick

3109.2 California Swimming Pool Safety Act (Statewide)

NOTE: These regulations are subject to local government modification. You should verify the applicable local government requirements at the time of application for a building permit.

The following text in this section contains the statutory language in the Swimming Pool Safety Act (HS Code, §§ 115920 — 115929) that is required to be duplicated and published in California Code of Regulations, Title 24. As such, the section numbers reflect those within the Health and Safety Code.

115920. This act shall be known and may be cited as the Swimming Pool Safety Act.

(Added by Stats. 1996, Ch. 925, Sec. 3.5. Effective January 1, 1997.)

115921. As used in this article the following terms have the following meanings:

- "Swimming pool" or "pool" means any structure intended for swimming or recreational bathing that contains water over 18 inches deep. "Swimming pool" includes in-ground and aboveground structures and includes, but is not limited to, hot tubs, spas, portable spas and nonportable wading pools.

- "Public swimming pool" means a swimming pool operated for the use of the general public with or without charge, or for the use of the members and guests of a private club. Public swimming pool does not include a swimming pool located on the grounds of a private single-family home.

- "Enclosure" means a fence, wall or other barrier that isolates a swimming pool from access to the home.

- "ANSI/APSP performance standard" means a standard that is accredited by the American National Standards Institute (ANSI) and published by the Association of Pool and Spa Professionals (APSP).

- "Suction outlet" means a fitting or fixture typically located at the bottom or on the sides of a swimming pool that conducts water to a recirculating pump.

[Amended by Stats. 2024, Ch 769 (SB 552) Effective January 1, 2025.]

115922.

- Except as provided in Section 115925, subject to subdivision (b), and consistent with Section 1596.814, when a building permit is issued for the construction of a new swimming pool or spa or the remodeling of an existing swimming pool or spa at a private single-family home, the respective swimming pool or spa shall be equipped with at least two of the following seven drowning prevention safety features:

  - An enclosure that meets the requirements of Section 115923 and isolates the swimming pool or spa from the private single-family home.

  - Removable mesh fencing that meets the ASTM International F2286 standard in conjunction with a gate that is self-closing and self-latching and can accommodate a key lockable device.

  - A manually operated or power-operated safety pool cover that is accompanied by a label verifying that the cover meets the specifications of the ASTM International F1346-23 standard.

  - Exit alarms on the private single-family home's doors and windows that provide direct access to the swimming pool or spa without any intervening enclosure. Whenever any door or window is opened or left ajar, exit alarms shall make either an audible, continuous alarm sound or a repeating verbal warning, such as a notification that "the door to the pool is open." An exit alarm may be battery operated or connected to the electrical wiring of the building.

  - A self-closing, self-latching device with a release mechanism placed no lower than 54 inches above the floor on the private single-family home's doors providing direct access to the swimming pool or spa.

  - An alarm in good repair and operable as designed that, when placed in a swimming pool or spa, will sound upon detection of accidental or unauthorized entrance into the water. The alarm shall meet and be independently certified to the ASTM International F2208 standard that includes surface motion, pressure, sonar, laser and infrared type alarms. A swimming protection alarm feature designed for individual use, including an alarm attached to a child that sounds when the child exceeds a certain distance or becomes submerged in water, is not a qualifying drowning prevention safety feature.

  - Other means of protection, if the degree of protection afforded is equal to or greater than that afforded by any of the features set forth above and has been independently verified by an approved testing laboratory as meeting standards for those features established by ASTM International, the American Society of Mechanical Engineers, or another nationally recognized standards development organization, and the feature is accompanied by a label verifying that the protection meets those standards.

- The requirements of subdivision (a) are not satisfied by any of the following:

  - An exit alarm and a self-closing, self-latching device on the same door.

  - An exit alarm and a door latch on separate doors.

  - A safety pool cover and an alarm described in paragraph (6) of subdivision (a).

- Before the issuance of a final approval for the completion of permitted construction or remodeling work, the local building code official shall inspect the drowning safety prevention features required by this section and, if no violations are found, shall give final approval.

[Amended by Stats. 2024, Ch. 745 (AB 2866) and Ch 769 (SB 552) Effective January 1, 2025.]

115923. An enclosure shall have all of the following characteristics:

- Any access gates through the enclosure open away from the swimming pool, and are self-closing with a self-latching device placed no lower than 60 inches above the ground.

- A minimum height of 60 inches.

- A maximum vertical clearance from the ground to the bottom of the enclosure of two inches.

- Gaps or voids, if any, do not allow passage of a sphere equal to or greater than four inches in diameter.

- An outside surface free of protrusions, cavities or other physical characteristics that would serve as handholds or footholds that could enable a child below the age of five years to climb over.

(Added by Stats. 1996, Ch. 925, Sec. 3.5. Effective January 1, 1997.)

115924.

- Any person entering into an agreement to build a swimming pool or spa, or to engage in permitted work on a pool or spa covered by this article, shall give the consumer notice of the requirements of this article.

- Pursuant to existing law, the Department of Health Services shall have available on the department's Web site, commencing January 1, 2007, approved pool safety information available for consumers to download. Pool contractors are encouraged to share this information with consumers regarding the potential dangers a pool or spa poses to toddlers. Additionally, pool contractors may provide the consumer with swimming pool safety materials produced from organizations such as the United States Consumer Product Safety Commission, Drowning Prevention Foundation, California Coalition for Children's Safety & Health, Safe Kids Worldwide, Association of Pool and Spa Professionals, or the American Academy of Pediatrics.

(Amended by Stats. 2006, Ch. 478, Sec. 3. Effective January 1, 2007.)

115925. The requirements of this article do not apply to any of the following:

- Public swimming pools.

- Hot tubs or spas with locking safety covers that comply with the ASTM International F1346 standard.

- An apartment complex or any residential setting other than a single-family home.

[Amended by Stats. 2024, Ch. 769 (SB 552) Effective January 1, 2025.]

115926

- The State Department of Social Services shall prescribe drowning prevention safety standards governing all swimming pools and other bodies of water located at facilities regulated by the department, regardless of whether the swimming pool is also subject to this article. The department may adopt higher drowning prevention safety standards than the requirements of this article. The department shall adopt regulations required by this section by January 1, 2027.

- Notwithstanding the rulemaking provisions of the Administrative Procedure Act [Chapter 3.5 (commencing with Section 11340) of Part 1 of Division 3 of Title 2 of the Government Code], the State Department of Social Services may implement, interpret, or make specific this article by means of interim licensing standards or similar written instructions until regulations are adopted. These interim licensing standards or similar written instructions shall have the same force and effect as regulations until January 1, 2027.

[Added by Stats. 2024, Ch. 745 (AB 2866) Effective January 1, 2025.]

115927. Notwithstanding any other provision of law, this article shall not be subject to further modification or interpretation by any regulatory agency of the state, this authority being reserved exclusively to local jurisdictions, as provided for in paragraph (7) subdivision (a) of Section 115922 and subdivision (c) of Section 115925.

[Amended by Stats. 2018, Ch. 957, Sec. 13. (SB 1078) Effective January 1, 2019.]

115928. Whenever a building permit is issued for the construction of a new swimming pool or spa, the pool or spa shall meet all of the following requirements:

  - The suction outlets of the pool or spa for which the permit is issued shall be equipped to provide circulation throughout the pool or spa as prescribed in paragraphs (2) and (3).

  - The swimming pool or spa shall either have at least two circulation suction outlets per pump that shall be hydraulically balanced and symmetrically plumbed through one or more "T" fittings, and that are separated by a distance of at least three feet in any dimension between the suction outlets, or be designed to use alternatives to suction outlets, including, but not limited to, skimmers or perimeter overflow systems to conduct water to the recirculation pump.

  - The circulation system shall have the capacity to provide a complete turnover of pool water, as specified in Section 3124B of Chapter 31B of the California Building Standards Code (Title 24 of the California Code of Regulations).

- Suction outlets shall be covered with anti-entrapment grates, as specified in the ANSI/APSP-16 performance standard or successor standard designated by the federal Consumer Product Safety Commission, that cannot be removed except with the use of tools. Slots or openings in the grates or similar protective devices shall be of a shape, area and arrangement that would prevent physical entrapment and would not pose any suction hazard to bathers.

- Any backup safety system that an owner of a new swimming pool or spa may choose to install in addition to the requirements set forth in subdivisions (a) and (b) shall meet the standards as published in the document, "Guidelines for Entrapment Hazards: Making Pools and Spas Safer," Publication Number 363, March 2005, United States Consumer Product Safety Commission.

[Amended by Stats. 2012, Ch. 679, Sec. 2. (AB 2114) Effective January 1, 2013.]

115928.5. Whenever a building permit is issued for the remodel or modification of an existing swimming pool, toddler pool or spa, the permit shall require that the suction outlet or suction outlets of the existing swimming pool, toddler pool or spa be upgraded so as to be equipped with anti-entrapment grates, as specified in the ANSI/APSP-16 performance standard or a successor standard designated by the federal Consumer Product Safety Commission.

[Amended by Stats. 2012, Ch. 679, Sec. 3. (AB 2114) Effective January 1, 2013.]

115929.

- The Legislature encourages a private entity, in consultation with the Epidemiology and Prevention for Injury Control Branch of the department, to produce an informative brochure or booklet, for consumer use, explaining the child drowning hazards of, possible safety measures for, and appropriate drowning hazard prevention measures for, home swimming pools and spas, and to donate the document to the department.

- The Legislature encourages the private entity to use existing documents from the United States Consumer Product Safety Commission on pool safety.

- If a private entity produces the document described in subdivisions (a) and (b) and donates it to the department, the department shall review and approve the brochure or booklet.

- Upon approval of the document by the department, the document shall become the property of the state and a part of the public domain. The department shall place the document on its Web site in a format that is readily available for downloading and for publication. The department shall review the document in a timely and prudent fashion and shall complete the review within 18 months of receipt of the document from a private entity.

(Added by Stats. 2003, Ch. 422, Sec. 3. Effective January 1, 2004.)

Section 3110 Automatic Vehicular Gates

3110.1 General

Automatic vehicular gates shall comply with the requirements of Sections 3110.2 and 3110.3 and other applicable sections of this code.

3110.2 Vehicular Gates Intended for Automation

Vehicular gates intended for automation shall be designed, constructed and installed to comply with the requirements of ASTM F2200.

3110.3 Vehicular Gate Openers

Vehicular gate openers, where provided, shall be listed in accordance with UL 325.

Section 3111 Solar Energy Systems

3111.1 General

Solar energy systems shall comply with the requirements of this section.

3111.1.1 Wind Resistance

Rooftop-mounted photovoltaic (PV) panel systems and solar thermal collectors shall be designed in accordance with Section 1609.

Exception: [DSA-SS, DSA-SS/CC, HCD-1, HCD-2] Rooftop-mounted photovoltaic (PV) panel systems and solar thermal collectors shall be designed in accordance with Section 1511.10 of this code.

3111.1.2 Roof Live Load

Roof structures that provide support for solar energy systems shall be designed in accordance with Section 1607.15.

3111.2 Solar Thermal Systems

Solar thermal systems shall be designed and installed in accordance with this section, the California Plumbing Code, the California Mechanical Code and the California Fire Code. Where light-transmitting plastic covers are used, solar thermal collectors shall be designed in accordance with Section 2606.12.

3111.2.1 Equipment

Solar thermal systems and components shall be listed and labeled in accordance with ICC 900/SRCC 300 and ICC 901/SRCC 100.

3111.3 Photovoltaic Solar Energy Systems

Photovoltaic solar energy systems shall be designed and installed in accordance with this section, the California Fire Code, the California Electrical Code and the manufacturer's installation instructions.

3111.3.1 Equipment

Photovoltaic panels and modules shall be listed and labeled in accordance with UL 1703 or with both UL 61730-1 and UL 61730-2. Inverters shall be listed and labeled in accordance with UL 1741. Systems connected to the utility grid shall use inverters listed for utility interaction.

3111.3.2 Fire Classification

Rooftop-mounted photovoltaic (PV) panel systems shall have a fire classification in accordance with Section 1505.9. Building-integrated photovoltaic (BIPV) systems installed as roof coverings shall have a fire classification in accordance with Section 1505.8.

3111.3.3 Building-Integrated Photovoltaic (BIPV) Systems

BIPV systems installed as roof coverings shall be designed and installed in accordance with Section 1507.

[F] 3111.3.4 Access and Pathways

Diagram

Roof access, pathways and spacing requirements shall be provided in accordance with Section 1205 of the California Fire Code.

UpCodes Diagrams (4)

PV: Setbacks and Pathways on R-3 Occ.

PV Setbacks: R-3 Occ.

PV: Pathways to Emerg. Egress Windows

PV: Setbacks and Pathways: Non R-3

3111.3.5 Elevated Photovoltaic (PV) Support Structures

Elevated PV support structures shall comply with either Section 3111.3.5.1 or 3111.3.5.2.

Exception: Elevated PV support structures that are installed over agricultural uses.

3111.3.5.1 Photovoltaic (PV) Panels Installed Over Open-Grid Framing or a Noncombustible Deck

Elevated PV support structures with PV panels installed over open-grid framing or over a noncombustible deck shall have PV panels tested, listed and labeled with a fire type rating in accordance with UL 1703 or with both UL 61730-1 and UL 61730-2. Photovoltaic panels marked "not fire rated" shall not be installed on elevated PV support structures.

3111.3.5.2 Photovoltaic (PV) Panels Installed Over a Roof Assembly

Diagram

Elevated PV support structures with a PV panel system installed over a roof assembly shall have a fire classification in accordance with Section 1505.9.

UpCodes Diagram (1)

Roof Assembly Fire Classification

3111.3.6 Ground-Mounted Photovoltaic (PV) Panel Systems

Ground-mounted photovoltaic panel systems shall be designed and installed in accordance with Chapter 16 and the California Fire Code.

3111.3.6.1 Fire Separation Distances

Ground-mounted photovoltaic panel systems shall be subject to the fire separation distance requirements determined by the local jurisdiction.

Section 3112 Greenhouses

3112.1 General

The provisions of this section shall apply to greenhouses that are designed and used for the cultivation, maintenance, or protection of plants.

[BE] 3112.2 Accessibility

Greenhouses shall be accessible in accordance with Chapter 11. [HCD 1] Greenhouses accessory to covered multifamily dwellings, as defined in Chapter 2, used as a common use facility, shall be on an accessible route in accordance with Chapter 11A.

3112.3 Structural Design

Greenhouses shall comply with the structural design requirements for greenhouses in Chapter 16.

Exception: [DSA-SS and DSA-SS/CC] Greenhouses considered to be school buildings shall comply with the structural design requirements in Chapter 16A and in accordance with Part 1, California Administrative Code, Title 24, CCR.

3112.4 Glass and Glazing

Diagram

Glass and glazing used in greenhouses shall comply with Section 2405.

UpCodes Diagram (1)

Glazing: Hazardous Locations

3112.5 Light-Transmitting Plastics

Light-transmitting plastics shall be permitted in lieu of plain glass in greenhouses and shall comply with Section 2606.

3112.6 Membrane Structures

Greenhouses that are membrane structures shall comply with Section 3102.

3112.6.1 Plastic Film

Plastic films used in greenhouses shall comply with Section 3102.3.

Section 3113 Relocatable Buildings

3113.1 General

The provisions of this section shall apply to relocatable buildings. Relocatable buildings manufactured after the effective date of this code shall comply with the applicable provisions of this code. [DSA-SS and DSA-SS/CC] as enforced by the enforcement agency.

Exception: This section shall not apply to manufactured housing used as dwellings.

[HCD] The provisions of Section 3113 are not applicable to commercial modulars, manufactured homes, mobilehomes, multi-unit manufactured housing and special purpose commercial modulars as defined in Health and Safety Code Sections 18001.8, 18007, 18008, 18008.7 and 18012.5, respectively. These structures are subject to installation/reinstallation requirements specified in the Mobilehome Parks Act (Health and Safety Code Section 18200 et seq.) and the California Code of Regulations, Title 25, Division 1, Chapter 2. Manufactured homes must meet unit identification (data plate) and certification label requirements as specified in the Code of Federal Regulations, Title 24, Subtitle B, Chapter XX, Part 3280 and Health and Safety Code Section 18032. Commercial modulars and special purpose commercial modulars must meet identification requirements in the California Code of Regulations, Title 25, Division 1, Chapter 3, Subchapter 2.

3113.1.1 Compliance

A newly constructed relocatable building shall comply with the requirements of this code for new construction. [DSA-SS and DSA-SS/CC] as enforced by the enforcement agency. An existing relocatable building that is undergoing alteration, addition, change of occupancy or relocation shall comply with Chapter 14 of the California Existing Building Code.

Exception: [DSA-SS and DSA-SS/CC] An existing relocatable public school building that is undergoing alteration, addition or change of occupancy shall comply with Chapter 3 of the California Existing Building Code.

3113.2 Supplemental Information

Supplemental information specific to a relocatable building shall be submitted to the authority having jurisdiction. It shall, as a minimum, include the following in addition to the information required by Section 105:

Exception: [DSA-SS and DSA-SS/CC] Supplemental information specific to a relocatable building shall be submitted to the enforcement agency. It shall, as a minimum, include the following in addition to the information required by Section 1603A:

- Manufacturer's name and address.

- Date of manufacture.

- Serial number of module.

- Manufacturer's design drawings.

- Type of construction in accordance with Section 602.

- Design loads including: roof live load, roof snow load, floor live load, wind load and seismic site class, use group and design category.

- Additional building planning and structural design data.

- Site-built structure or appurtenance attached to the relocatable building.

3113.3 Manufacturer's Data Plate

Each relocatable module shall have a data plate that is permanently attached on or adjacent to the electrical panel, and shall include the following information:

- Occupancy group.

- Manufacturer's name and address.

- Date of manufacture.

- Serial number of module.

- Design roof live load, design floor live load, snow load, wind and seismic design.

- Approved quality assurance agency or approved inspection agency.

- Codes and standards of construction.

- Envelope thermal resistance values.

- Electrical service size.

- Fuel-burning equipment and size.

- Special limitations if any.

Exception: [DSA-SS and DSA-SS/CC] Each relocatable module shall have two metal identification labels permanently attached to the structure as enforced by the enforcement agency.

3113.4 Inspection Agencies

The building official is authorized to accept reports of inspections conducted by approved inspection agencies during off-site construction of the relocatable building, and to satisfy the applicable requirements of Sections 110.3 through 110.3.12.1.

Exception: [DSA-SS and DSA-SS/CC] Each relocatable module shall be inspected during construction and installation at the project site by project inspectors acceptable to the enforcement agency in accordance with Part 1, California Administrative Code, Title 24, CCR.

Section 3114 Intermodal Shipping Containers

[OSHPD 1, 1R, 2, 4 & 5] Not permitted by OSHPD.

3114.1 General

The provisions of Section 3114 and other applicable sections of this code shall apply to intermodal shipping containers that are repurposed for use as buildings or structures, or as a part of buildings or structures.

Exceptions: [DSA-SS & DSA-SS/CC] Not permitted by DSA.

- Intermodal shipping containers previously approved as existing relocatable buildings complying with Chapter 14 of the California Existing Building Code.

- Stationary storage battery arrays located in intermodal shipping containers complying with Chapter 12 of the California Fire Code.

- Intermodal shipping containers that are listed as equipment complying with the standard for equipment, such as air chillers, engine generators, modular data centers, and other similar equipment.

- Intermodal shipping containers housing or supporting experimental equipment are exempt from the requirements of Section 3114, provided that they comply with all of the following:

  - Such units shall be single stand-alone units supported at grade level and used only for occupancies as specified under Risk Category I in Table 1604.5.

  - Such units are located a minimum of 8 feet (2438 mm) from adjacent structures, and are not connected to a fuel gas system or fuel gas utility.

  - In hurricane-prone regions and flood hazard areas, such units are designed in accordance with the applicable provisions of Chapter 16.

- [HCD] Shipping containers constructed or converted off-site that meet the definition of Factory-built Housing in Health and Safety Code Section 19971 or Commercial Modular(s) as defined in Health and Safety Code Section 18001.8 shall be approved by the Department of Housing and Community Development.

3114.2 Construction Documents

The construction documents shall contain information to verify the dimensions and establish the physical properties of the steel components and wood floor components of the intermodal shipping container, in addition to the information required by Sections 107 and 1603.

3114.3 Intermodal Shipping Container Information

Intermodal shipping containers shall bear an existing data plate containing the following information as required by ISO 6346 and verified by an approved agency. A report of the verification process and findings shall be provided to the building owner.

- Manufacturer's name or identification number.

- Date manufactured.

- Safety approval number.

- Identification number.

- Maximum operating gross mass or weight (kg) (lbs).

- Allowable stacking load for 1.8G (kg) (lbs).

- Transverse racking test force (Newtons).

- Valid maintenance examination date.

Where approved by the building official, the markings and existing data plate are permitted to be removed from the intermodal shipping containers before they are repurposed for use as buildings or structures or as a part of buildings or structures.

3114.4 Protection Against Decay and Termites

Wood structural floors of intermodal shipping containers shall be protected from decay and termites in accordance with the applicable provisions of Section 2304.12.1.1.

3114.5 Under-Floor Ventilation

The space between the bottom of the floor joists and the earth under any intermodal shipping container, except spaces occupied by basements and cellars, shall be provided with ventilation in accordance with Section 1202.4.

3114.6 Roof Assemblies

Intermodal shipping container roof assemblies shall comply with the applicable requirements of Chapter 15.

Exception: Single-unit, stand-alone intermodal shipping containers not attached to, or stacked vertically over, other intermodal shipping containers, buildings or structures. [DSA-SS & DSA-SS/CC] Not permitted by DSA.

3114.7 Joints and Voids

Joints and voids that create concealed spaces between connected or stacked intermodal shipping containers at fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected by an approved fire-resistant joint system in accordance with Section 715.

3114.8 Structural

Intermodal shipping containers that conform to ISO 1496-1 and are repurposed for use as buildings or structures, or as a part of buildings or structures, shall be designed in accordance with Chapter 16 and this section.

3114.8.1 Foundations and Supports

Intermodal shipping containers repurposed for use as a permanent building or structure shall be supported on foundations or other supporting structures designed and constructed in accordance with Chapters 16 through 23.

3114.8.1.1 Anchorage

Intermodal shipping containers shall be anchored to foundations or other supporting structures as necessary to provide a continuous load path for all applicable design and environmental loads in accordance with Chapter 16.

3114.8.1.2 Stacking

Intermodal shipping containers used to support stacked units shall comply with Section 3114.8.4.

3114.8.2 Welds

The strength of new welds and connections shall be of not less than the strength provided by the original connections. All new welds and connections shall be designed and constructed in accordance with Chapters 16, 17 and 22.

3114.8.3 Structural Design

The structural design for the intermodal shipping containers repurposed for use as a building or structure, or as part of a building or structure, shall comply with Section 3114.8.4 or 3114.8.5.

3114.8.4 Detailed Design Procedure

A structural analysis meeting the requirements of this section shall be provided to the building official to demonstrate the structural adequacy of the intermodal shipping containers.

Exception: Structures using an intermodal shipping container designed in accordance with Section 3114 8.5.

3114.8.4.1 Material Properties

Structural material properties for existing intermodal shipping container steel components shall be established by Section 2202.

3114.8.4.2 Seismic Design Parameters

The seismic force-resisting system shall be designed and detailed in accordance with ASCE 7 and one of the following:

- Where all or portions of the profiled steel panel elements are considered to be the seismic force-resisting system, design and detailing shall be in accordance with the AISI S100 and ASCE 7, Table 12.2-1 requirements for steel systems not specifically detailed for seismic resistance, excluding cantilever column systems. [DSA-SS & DSA-SS/CC] Not permitted by DSA.

- Where all or portions of the profiled steel panel elements are not considered to be part of the seismic force-resisting system, an independent seismic force-resisting system shall be selected and detailed in accordance with ASCE 7, Table 12.2-1.

- Where all or portions of the profiled steel panel elements are retained and integrated into a seismic force-resisting system other than as permitted by Item 1, seismic design parameters shall be developed from testing and analysis in accordance with Section 104.2.3 and ASCE 7, Section 12.2.1.1 or 12.2.1.2.

3114.8.4.3 Allowable Shear Value

The allowable shear values for the profiled steel panel side walls and end walls shall be determined in accordance with the design approach selected in Section 3114.8.4.2. Where penetrations are made in the side walls or end walls designated as part of the lateral force-resisting system, the penetrations shall be substantiated by rational analysis.

3114.8.5 Simplified Structural Design Procedure of Single-Unit Containers

Single-unit intermodal shipping containers conforming to the limitations of Section 3114.8.5.1 shall be permitted to be designed in accordance with Sections 3114.8.5.2 and 3114.8.5.3. [DSA-SS & DSA-SS/CC] Not permitted by DSA.

3114.8.5.1 Limitations

The use of Section 3114.8.5 is subject to the following limitations:

- The intermodal shipping container shall be a single-unit, stand-alone unit supported on a foundation and shall not be in contact with or supporting any other shipping container or other structure.

- The intermodal shipping container top and bottom rails, corner castings, and columns or any portion thereof shall not be notched, cut, or removed in any manner.

- The intermodal shipping container shall be erected in a level and horizontal position with the floor located at the bottom.

- The intermodal shipping container shall be located in Seismic Design Category A, B, C or D.

3114.8.5.2 Structural Design Assumptions

Where permitted by Section 3114.8.5.1, single-unit, stand-alone intermodal shipping containers shall be designed using the following assumptions for the profile steel panel lateral-force resisting system:

- The appropriate detailing requirements contained in Chapters 16 through 23.

- Response modification coefficient, R = 2.

- Overstrength factor, Ω0 = 2.5.

- Deflection amplification factor, Cd = 2.

- Limits on structural height, hn = 9.5 feet (2900 mm).

3114.8.5.3 Allowable Shear

The allowable shear for the profiled steel panel side walls (longitudinal) and end walls (transverse) for wind design and seismic design using the coefficients of Section 3114.8.5.2 shall be in accordance with Table 3114.8.5.3, provided that all of the following conditions are met:

- The total linear length of all openings in any individual side wall or end wall shall be limited to not more than 50 percent of the length of that side wall or end wall, as shown in Figure 3114.8.5.3(1).

- Any full-height wall length, or portion thereof, less than 4 feet (305 mm) shall not be considered as a portion of the lateral force-resisting system, as shown in Figure 3114.8.5.3(2).

- All side walls or end walls used as part of the lateral force-resisting system shall have an existing or new boundary element on all sides to form a continuous load path, or paths, with adequate strength and stiffness to transfer all forces from the point of application to the final point of resistance, as shown in Figure 3114.8.5.3(3).

- Where openings are made in intermodal shipping container walls, floors or roofs, for doors, windows and other openings:

  - 4.1.   The openings shall be framed with steel elements that are designed in accordance with Chapters 16 and 22.

  - 4.2.   The cross section and material grade of any new steel element shall be equal to or greater than the steel element removed.

- A maximum of one penetration not greater than 6 inches (152 mm) in diameter for conduits, pipes, tubes or vents, or not greater than 16 square inches (10 323 mm2) for electrical boxes, is permitted for each individual 8-foot (2438 mm) length of lateral force-resisting wall. Penetrations located in walls that are not part of the lateral force-resisting system shall not be limited in size or quantity. Existing intermodal shipping container vents shall not be considered a penetration, as shown in Figure 3114.8.5.3(4).

- End wall doors designated as part of the lateral force-resisting system shall be intermittently welded closed around the full perimeter of the door panels.

TABLE 3114.8.5.3—ALLOWABLE SHEAR VALUES FOR PROFILED STEEL PANEL SIDE WALLS AND END WALLS FOR WIND OR SEISMIC LOADING

| CONTAINER DESIGNATIONb | CONTAINER DIMENSION (nominal length) | CONTAINER DIMENSION (nominal height) | ALLOWABLE SHEAR VALUES (PLF)a, c |  |
| --- | --- | --- | --- | --- |
|  |  |  | Side Wall | End Wall |
| 1EEE | 45 feet | 9.5 feet | 75 | 843 |
| 1EE |  | 8.5 feet |  |  |
| 1AAA | 40 feet | 9.5 feet | 84 |  |
| 1AA |  | 8.5 feet |  |  |
| 1A |  | 8.0 feet |  |  |
| 1AX |  | < 8.0 feet |  |  |
| 1BBB | 30 feet | 9.5 feet | 112 |  |
| 1BB |  | 8.5 feet |  |  |
| 1B |  | 8.0 feet |  |  |
| 1BX |  | < 8.0 feet |  |  |
| 1CC | 20 feet | 8.5 feet | 168 |  |
| 1C |  | 8.0 feet |  |  |
| 1CX |  | < 8.0 feet |  |  |
| 1D | 10 feet | 8.0 feet | 337 |  |
| 1DX |  | < 8.0 feet |  |  |

For SI: 1 foot = 304.8 mm.

- The allowable strength shear values for the side walls and end walls of the intermodal shipping containers are derived from ISO 1496-1 and reduced by a factor of safety of 5.

- Container designation type is derived from ISO 668.

- Limitations of Sections 3114.8.5.1 and 3114.8.5.3 shall apply.

FIGURE 3114.8.5.3(1)—BRACING UNIT DISTRIBUTION—MAXIMUM LINEAR LENGTH

FIGURE 3114.8.5.3(2)—BRACING UNIT DISTRIBUTION—MINIMUM LINEAR LENGTH

For SI: 1 foot = 304.8 mm.

FIGURE 3114.8.5.3(3)—BRACING UNIT DISTRIBUTION—BOUNDARY ELEMENTS

FIGURE 3114.8.5.3(4)—BRACING UNIT DISTRIBUTION—PENETRATION LIMITATIONS

For SI: 1 foot = 304.8 mm.

3114.9 Additional Requirements [DSA-SS and DSA-SS/CC]

3114.9.1 General

- Intermodal shipping containers shall not have been manufactured earlier than 24 months from the date of DSA approval of the site-specific or stockpile building design drawings.

- Intermodal shipping containers shall be undamaged and have no previous repairs. The acceptable tolerances shall not exceed those given in the ANSI/AISC 303—16: Code of Standard Practice for Steel Buildings and Bridges.

- Intermodal shipping container type shall be standard dry cargo container, used for the transportation of dry goods only. Containers shall not have been used for transporting hazardous materials. Containers shall not have been painted with paint containing lead.

- All structural elements and details shall be justified through engineering calculations in accordance with the California Administrative Code (Title 24, Part 1, CCR) Section 4-317(d).

3114.9.2 Structural Integrity Verification

Each intermodal shipping container shall have selection, structural integrity verification, general condition assessment, inspection and testing as enforced by the enforcement agency.

3114.9.3 Seismic Design Requirements

- The container steel frame contribution to the lateral force resistance shall be neglected even in cases where the container siding is removed.

- Deformation compatibility of structural elements that are not included in the seismic force-resisting system shall be considered in the analysis and when evaluating stiffness irregularities.

- The total length of siding (less openings) along a line in a lower story shall not be less than 80 percent of the total length of siding (less openings) along the same line in the story immediately above.